## Ažuriranja MCCa
Rd.br. | Ormar | Datum | Opis | Status | Napomena | Oprema
1mj.26. NAPOMENE
8mj.25. NAPOMENE
1. | MCC Normal 4LKD002AR | 20.08.2025. | Izvod "FAST FILING PUMP" - sa 22kW na 11kW - potrebno postaviti novu motorku i sklopnik | - NE UCRTAVATI JOŠ doći će do promjene | provjeri je li naručena oprema | GV2P22+GVAE11+GVAD0110 LC1D25P7+LADN31+LAD4RCU
2. | MCC Normal 4LKD003AR | 11.08.2025. | Novi izvod: CHAIN CONVEYOR FOR BOTTOM ASH - 4 FDR 009 MO - 4KW (dvosmjerni) | - ucrtano u EPLAN (na zadnje mjesto) - naručiti opremu | provjeri je li naručena oprema
3. | MCC Emergency 4LKF002AR | 11.08.2025. | Novi izvod: "Grate expansion tank system" (nemamo tehničke podatke) SYSTÈME DE RÉSERVOIR D'EXPANSION À GRILLE | - ucrtano u EPLAN (na zadnje mjesto) - naručiti opremu | provjeri je li naručena oprema | SE.18727 + SE.19072 SOC.47506030 + SOC.47290590
4. | MCC Emergency 4LKF002AR | 11.08.2025. | Izvod: "EXPANSION TANK SYSTEM" - prebačen na 10kW | - ucrtano u EPLAN
5. | MCC - svi | 20.08.2025. | Potrebno je sve holdere za oznake tipkala prebaciti iz ZBZ32 na ZBZ33 (8x27 -> 18x27) | - potrebno ucrtati u Eplan (nekada ako)
Naknadno potrebno napraviti na terenu
Rd.br. | Ormar | DT | Stari part | Novi part | Napomena | Napomena
| 4LKF002AR | Q 093 04 | izvod pretpostavljen 32A | SE.18727 + SE.19072 SOC.47506030 + SOC.47290590
promjena 07.01.2026. -> uvršteno u listu potrošača
Rd.br. | Ormar | DT | Stari part | Novi part | Napomena | Pozicija potrošača | Oprema | Oprema - sklopnik | STATUS
| 4LKD001AR |  | FAST FILING PUMP - 11kW - na frekventni mora ići | obavezno na VFD |  | prebaciti u MCC Emergency na SPARE poziciju | C10F3TM050 + LV429515 + LV429515 | SIE.6SL3220-3YE26-0AF0 | Dodati postojeći 11kW VFD u MCC Emergency
| 4LKD007AR - VFD | 4 SEO 209 PO | [4 SEO 209 PO] WASTE WATER PUMP 1 - neutralizacijska | makni VFD -> postavi na sklopnik 3kW | OLD - 11kW frekventni | MCC Normal (novi ormar) | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) | DOL
| 4LKD007AR - VFD | 4 SEO 213 PO | [4 SEO 213 PO] WASTE WATER PUMP 2- neutralizacijska | makni VFD -> postavi na sklopnik 3kW | OLD - 11kW frekventni | MCC Normal (novi ormar) | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) | DOL
| 4LKD007AR - VFD | 4 SEO 264 PO | [4 SEO 264 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 1 - teški metal | makni VFD -> postavi na sklopnik | OLD - 5,5kW frekventni | MCC Normal (novi ormar) | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) | DOL
| 4LKD007AR - VFD | 4 SEO 269 PO | [4 SEO 269 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 2 - teški metal | makni VFD -> postavi na sklopnik | OLD - 5,5kW frekventni | MCC Normal (novi ormar) | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) | DOL
ATEP | 4LKF003AR | 4 CTE 063 PO | [4 CTE 063 PO] COOLING WATER PUMP 1 | prebaciti na VFD 5,5kW (gore izbačene) | po Zvoni: ostavi di je | prebaci u MCC emergency poziciju 5.5 kW starog potrošača
ATEP | 4LKF004AR | 4 CTE 064 PO | [4 CTE 064 PO] COOLING WATER PUMP 2 | prebaciti na VFD 5,5kW (gore izbačene) | po Zvoni: ostavi di je | prebaci u MCC emergency poziciju 5.5 kW starog potrošača
SFA | 4LKF005AR - VFD | 4 CRE 189 MO 4CRF188PO | [4 CRE 189 MO] COOLING WATER PUMP 1 | obavezno na VFD | 37kW - postojeće
SFA | 4LKF005AR - VFD | 4 CRE 196 MO 4CRF195PO | [4 CRE 196 MO] COOLING WATER PUMP 2 | obavezno na VFD | 37kW - postojeće

## Boiler MCC distribution
Napomena | Boiler MCC 4LKD001AR |  |  | BOILER/LOW VOLTAGE CABINET BOILER (NORMAL) | CHAUDIÈRE/ARMOIRE BASSE TENSION CHAUDIÈRE (NORMALE) | [6 empty] | spare 25% -> postavljeno 30% |  |  | 25kA! | 36kA |  | prema tablici | [9 empty] | prema tablici
| Oznaka EPLAN | KKS OLD | KKS prekidača | KKS NEW | KKS NEW - prijevod | PID | 1Ph/3Ph | V | kW | EPLAN kW | kA | Struja motora [A] | Simultaneity factor in maximal normal mode [%] | Struja prekidača s faktorom [A] | Dovodni prekidač/rastavljač SIEMENS | Dovodni prekidač/rastavljač SCHNEIDER | Reverzibilni | Motorna zaštita Siemens | Motorna zaštita A Siemens | Motorna zaštita AUX Siemens | Sklopnik minimum 12A Siemens | Sklopnik AUX + RC element Siemens | Soft starter SIEMENS | Soft starter SCHNIDER | Frekventni | Motorna zaštita Schneider | Motorna zaštita A Schneider | Sklopnik minimum 12A Schneider | 1F Strujni trafo ampermetar | Mjerni strujni trafo za 3F el. Measurement - Socomec | Dozemni spoj - Socomec | Mjerni strujni trafo za 3F el. Measurement - Siemens | Dozemni spoj - Siemens | Prekidač za 230VAC | Prekidač za 48VAC | RELEJ 48VAC minimum 6A | RELEJ 230VAC minimum 6A | Safety relay | Tip kabela | Strujno opterećenje kabela | vanjski promjer kabela | Rastavna sklopka | Proizvođač motora | Klematura | Napomena
| ORMAR 1 2100+200x1000x600 | DOVOD | =4LKD001AR+4LKD001AR | [8 empty] | 213.291 |  | 163.8832 | 3KD3632-0NE10-0(200A) SIE.3KD9103-5 (AUX) 3KD9204-7 (cable cover) | C25B3TM250 + LV432597T + 2x LV432593
[16 empty] | INS 250 - 31106 29450 (NO/NC) 2xLV429518 (cover) | [25 empty] | LV481453 -> ispod ide odvodnik prenapona
|  |  | Predikač prije odvodnika - | [26 empty] | 3x 48290573
Odvodnik prenapona - 5SD7473-1
Nadzor faza - 3UG5514-1BR20
Okretno polje -
| ORMAR 2 2100+200x1000x600 |  | =4LKD001AR+4LKD002AR | [5 empty] | 23 | 23 |  | 53.547 |  | 22.3626 | 3VA1063-3ED32-0AA0 - 63A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM100 - 100A 36kA +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita)
| -F11 - SPARE | FAST FILING PUMP | SPARE BIO JE: [4 SDX 001 PO] FAST FILING PUMP | [38 empty] | LV481603 + GS1AH103 + ZBE101 + GS1AM110
| -F12 | CLOSED CHAIN CONVEYOR 1 | 4 FES 004 MO | [4 FES 004 MO] MAIN CLOSED CHAIN CONVEYOR | CONVOYEUR PRINCIPAL À CHAÎNE FERMÉ | Ash system | 3Ph | 400 | 1.5 | 1.5 |  | 2.17 | 80 | 1.736 |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F13 | Screw conveyor | 4 FES 002 MO | [4 FES 002 MO] REVERSING SCREW CONVEYOR BELOW EX. ECO | CONVOYEUR À VIS SOUS L'ÉCO | Ash system | 3Ph | 400 | 1.5 | 1.5 |  | 2.17 | 80 | 1.736 |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F14 | SPARE (prazni prostor) | 4FGO-CR-101 | BURNER SYSTEM | SYSTEME DE BRÛLEUR |  | 3Ph | 400 | 20 | 20 |  | 28.9 | 20 | 5.78 | C10F3TM032 - 32A +29450 (1CO) +LV429337T (rotary) +2x LV429517 (duga zaštita) | NG125 - 18727 - 32A +19072 (1CO) | [14 empty] | 47506015 | [7 empty] | U1000R2V 4G6 |  | 14.3
| -F15 | SPARE (prazni prostor) | 4 FES 005 MO | [4 FES 005 MO] OVERBAND MAGNETIC SEPARATOR | SEPARATEUR MAGNETIQUE |  | 3Ph | 400 | [6 empty] | C10B3TM016 - 16A +29450 (1CO) +LV429337T (rotary) +2x LV429517 (duga zaštita) | NG125 - 18724 - 16A +19072 (1CO) | [14 empty] | 47506015 | [7 empty] | U1000R2V 4G2,5 |  | 11.1 |  | NORD
| -F16 |  | 4 FDR 005 BJ | COOLING OIL PUMP AND FAN MOTOR | POMPE À HUILE DE REFROIDISSEMENT ET MOTEUR DE VENTILATEUR |  | 3Ph | 400 | 1.5 | 1.5 |  | 2.17 | 100 | 2.17 | C10B3TM016 - 16A +29450 (1CO) +LV429337T (rotary) +2x LV429517 (duga zaštita) | NG125 - 18724 - 16A +19072 (1CO) | [9 empty] | Možda 10.04.2026. GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | Možda 10.04.2026. LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 | [7 empty] | U1000R2V 4G2,5 |  | 11.1
| -F17 |  | 4 SAR 200 BC | PNEUMATIC RAPPING SYSTEM | SYSTÈME DE RAPPEL PNEUMATIQUE |  | 3Ph | 400 | [6 empty] | C10B3TM016 - 16A +29450 (1CO) +LV429337T (rotary) +2x LV429517 (duga zaštita) | NG125 - 18724 - 16A +19072 (1CO) | [14 empty] | 47506015 | [7 empty] | U1000R2V 4G2,5 |  | 11.1
| -F18 |  | 4 FES 100 BC | WATER SPRAYING SYSTEM | SYSTÈME DE PULVÉRISATION D'EAU |  | 3Ph | 400 | 4 | UBACITI U SHEME i naručiti opremu |  | 5.78 | 100 | 5.78 | C10B3TM016 - 16A +29450 (1CO) +LV429337T (rotary) +2x LV429517 (duga zaštita) | NG125 - 18724 - 16A +19072 (1CO) | [14 empty] | 47506015 | [7 empty] | U1000R2V 4G2,5 |  | 11.1
| -F19 |  |  | SPARE (prazni prostor za izvod, samo prekidač)
| -F19.1 |  |  | SPARE (prazni prostor za izvod, samo prekidač)
| -F19.2 |  |  | SPARE (prazni prostor za izvod, samo prekidač)
| ORMAR 3 2100+200x1000x600 |  | =4LKD001AR+4LKD003AR | [5 empty] | 9.5 | 9.5 |  | 35.698 |  | 33.0668 | 3VA1063-3ED32-0AA0 - 63A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F21 | BELT CONVEYOR FOR BOTTOM ASH | 4 FES 008 MO | [4 FES 008 MO] BELT CONVEYOR FOR BOTTOM ASH | CONVOYEURS À BANDES APRÈS EXTRACTEURS À MÂCHEFERS | Ash system | 3Ph | 400 | 5.5 | 5.5 |  | 7.95 | 80 | 6.36 |  |  | ☑ | 3RV2021-1KA10 | 9 - 12.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G25 | 42 | 22.8 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F22 | ASH CRUSHER 1 | 4 FES 038 MO | [4 FES 038 MO] ASH CRUSHER BELOW EX. ECO | BROYEUR DE CENDRES SOUS L'ÉCO | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F23 | ASH CRUSHER 2 | 4 FES 040 MO | [4 FES 040 MO] ASH CRUSHER BELOW SH 3 | BROYEUR DE CENDRES SOUS LE SH 3 | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F24 | CLOSED CHAIN CONVEYOR 2 | 4 FES 050 MO | [4 FES 050 MO] CLOSED CHAIN CONVEYOR UNDER ECO | CONVOYEUR À CHAÎNE SOUS L'ÉCO | Ash system | 3Ph | 400 | 1.5 | 1.5 |  | 2.17 | 80 | 1.736 |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F25 | CHAIN CONVEYOR FOR BOTTOM ASH | 4 FDR 009 MO | CHAIN CONVEYOR FOR BOTTOM ASH | CONVOYEUR À CHAINE VERS ÉVACUATION DES CENDRES SOUS CHAUDIÈRE | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | [8 empty] | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F26 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 4 2100+200x1000x600 |  | =4LKD001AR+4LKD004AR | [5 empty] | 17 | 17 |  | 31.954 |  | 23.8758 | 3VA1063-3ED32-0AA0 - 63A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F31 | Chain conveyor for distribution | 4 FES 024 MO | [4 FES 024 MO] CHAIN CONVEYOR FOR DISTRIBUTION | CONVOYEUR À CHAINE VERS HALL DE STOCKAGE MÂCHEFERS | Ash system | 3Ph | 400 | 5.5 | 5.5 |  | 7.95 | 100 | 7.95 | NOVO |  | ☑ | 3RV2021-1KA10 | 9 - 12.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 42 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F32 | Rotary dispenser 1 | 4 FES 012 MO | [4 FES 012 MO] ROTARY DISPENSER BELOW EX. ECO | SAS ROTATIF SOUS L'ÉCO | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F33 | Rotary dispenser 2 | 4 FES 014 MO | [4 FES 014 MO] ROTARY DISPENSER BELOW SH 3 | DISTRIBUTEUR ROTATIF SOUS LE SH 3 | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F34 | CLOSED CHAIN CONVEYOR 3 | 4 FES 010 MO | [4 FES 010 MO] CLOSED CHAIN CONVEYOR FOR ASH DISPATCH | CONVOYEUR À CHAINE VERS ÉVACUATION DES CENDRES SOUS CHAUDIÈRE | Ash system | 3Ph | 400 | 1.5 | 1.5 |  | 2.17 | 80 | 1.736 |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
korigiran potrošač 13.07.2026. | -F35 | SPARE (prazni prostor) | BIO JE: SPARE (prazan prostor) 4SAR902MO | [4SAR902MO] FURNACE REFRACTORY COOLING FANS 1 | VENTILATEURS DE REFROIDISSEMENT RÉFRACTAIRES POUR FOURNAISE 1 |  | 3Ph | 400 | 4 | 4 |  | 5.78 | [13 empty] | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP
| -F36 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 5 2100+200x1000x600 |  | =4LKD001AR+4LKD005AR | [5 empty] | 14 | 14 |  | 26.312 |  | 26.312 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F41 | ASH CRUSHER 3 | 4 FES 042 MO | [4 FES 042 MO] ASH CRUSHER BELOW SH 2 | BROYEUR DE CENDRES SOUS LE SH 2 | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F42 | ASH CRUSHER 4 | 4 FES 044 MO | [4 FES 044 MO] ASH CRUSHER BELOW SH 1 | BROYEUR DE CENDRES SOUS LE SH 1 | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F43 | Rotary dispenser 3 | 4 FES 016 MO | [4 FES 016 MO] ROTARY DISPENSER BELOW SH 2 | SAS ROTATIF SOUS LE SH 2 | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F44 | Rotary dispenser 4 | 4 FES 018 MO | [4 FES 018 MO] ROTARY DISPENSER BELOW SH 1 | SAS ROTATIF SOUS LE SH 1 | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F45 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| -F46 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 6 2100+200x1000x600 |  | =4LKD001AR+4LKD006AR | [5 empty] | 14 | 14 |  | 33.826 |  | 26.312 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F51 | ASH CRUSHER 5 | 4 FES 046 MO | [4 FES 046 MO] ASH CRUSHER BELOW ECO 1 | BROYEUR DE CENDRES SOUS L'ÉCO 1 | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F52 | ASH CRUSHER 6 | 4 FES 048 MO | [4 FES 048 MO] ASH CRUSHER BELOW ECO 2 | BROYEUR DE CENDRES SOUS L'ÉCO 2 | Ash system | 3Ph | 400 | 4 | 4 |  | 5.78 | 100 | 5.78 |  |  | ☑ | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | 3RW4024-1BB14 | SE.ATS22D17Q |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F53 | Rotary dispenser 5 | 4 FES 020 MO | [4 FES 020 MO] ROTARY DISPENSER BELOW ECO 1 | SAS ROTATIF SOUS L'ÉCO 1 | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
| -F54 | Rotary dispenser 6 | 4 FES 022 MO | [4 FES 022 MO] ROTARY DISPENSER BELOW ECO 2 | SAS ROTATIF SOUS L'ÉCO 2 | Ash system | 3Ph | 400 | 3 | 3 |  | 4.34 | 100 | 4.34 |  |  | ☑ | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 | NORD
korigiran potrošač 13.07.2026. | -F55 | SPARE (prazni prostor) | BIO JE: SPARE (prazan prostor) | [4SAR908MO] FURNACE REFRACTORY COOLING FANS 2 | VENTILATEURS DE REFROIDISSEMENT RÉFRACTAIRES POUR FOURNAISE 2 |  | 3Ph | 400 | 4 | 4 |  | 5.78 | [13 empty] | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP
| -F56 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 7 2100+200x1000x600 -umjesto VFD ormara koji je premješten na emergency |  | =4LKD001AR+4LKD008AR novi 08.01.2026. | [5 empty] | 17 | 0 |  | 31.954 |  | 31.954 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM050 + LV429337T + LVS04033 +LV429515 50A je mislim dovoljno ako ješ popunimo spare
| -F61 |  | 4 SEO 209 PO | [4 SEO 209 PO] WASTE WATER PUMP 1 | POMPE D'EAUX USÉES 1 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 3 | potrebno ucrtati i naručiti opremu |  | 4.34 | 100 | 4.34 |  |  |  | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 |  |  | DOL
| -F62 |  | 4 SEO 264 PO | [4 SEO 264 PO] ASH PIT PUMP 1 | POMPE BOX MACHEFERS VERS EXTRACTEUR MÂCHEFERS 1 | frekventni | 3Ph | 400 | 5.5 | potrebno ucrtati i naručiti opremu |  | 7.95 | 100 | 7.95 |  |  |  | 3RV2021-1JA10 | 7 - 10A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 |  |  | DOL
| -F63 |  | 4 SEO 213 PO | [4 SEO 213 PO] WASTE WATER PUMP 2 | POMPE D'EAUX USÉES 2 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 3 | potrebno ucrtati i naručiti opremu |  | 4.34 | 100 | 4.34 |  |  |  | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 |  |  | DOL
| -F64 |  | 4 SEO 269 PO | [4 SEO 269 PO] ASH PIT PUMP 2 | POMPE BOX MACHEFERS VERS EXTRACTEUR MÂCHEFERS 2 | frekventni | 3Ph | 400 | 5.5 | potrebno ucrtati i naručiti opremu |  | 7.95 | 100 | 7.95 |  |  |  | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) 3RT2015-1AP02 (1NC) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) |  |  |  | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | 2x LC1D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) LAD9R1V (intelock blokada) |  |  | 47506015 |  | 3UF7011-1AU00-1 - base unit 3UF7510-1AA00-0 - ground fault 3UL2302-1A - trafo 35mm | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1 | LV481603 + GS1AH103 + ZBE101 + GS1AM110 |  |  | DOL
| -F55 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| -F56 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| Širina | Širina | 8000
|  |  |  | [4 SEO 209 PO] WASTE WATER PUMP 1 |  |  |  |  | 11 | nesto tu ne stima, treba provjeriti (29.06.26)
|  |  |  | [4 SEO 213 PO] WASTE WATER PUMP 2 |  |  |  |  | 11 | nesto tu ne stima, treba provjeriti (29.06.26)
3
| ORMAR 7 - VFD 2100+200x1600x600 |  | =4LKD001AR+4LKD007AR | [5 empty] | 44 | 44 |  | 73.4942 |  | 73.4942 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F61 - SPARE |  | 4 SEO 209 PO | [4 SEO 209 PO] WASTE WATER PUMP 1 | POMPE D'EAUX USÉES 1 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 11 | 11 | 5 | 15.9 | 100 | 15.9 | NSX 50A | C10F3TM050 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506030
| -F62 - SPARE |  | 4 SEO 264 PO | [4 SEO 264 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 1 | POMPE DU RÉSERVOIR DE CENDRES 1 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015
| -F63 - SPARE |  | 4 SEO 213 PO | [4 SEO 213 PO] WASTE WATER PUMP 2 | POMPE D'EAUX USÉES 2 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 11 | 11 | 5 | 15.9 | 0 | 0 | NSX 50A | C10F3TM050 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506030
| -F64 - SPARE |  | 4 SEO 269 PO | [4 SEO 269 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 2 | POMPE DU RÉSERVOIR DE CENDRES 2 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015
| -F65 NOVE |  | 4 FGO 003 MO | 4 FGO 003 MO LIGHT FUEL OIL PUMP 1 | 4 FGO 003 MO POMPE À FIOUL LÉGER 1 | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015
| -F65 NOVE |  | 4 FGO 004 MO | 4 FGO 004 MO LIGHT FUEL OIL PUMP 2 | 4 FGO 004 MO POMPE À FIOUL LÉGER 2 | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015
Note on M3: Luka Božićević: spare 30% struje
Note on O3: Luka Božićević: spare 30% struje
Note on P3: Luka Božićević: SCHNIDER: C25B3TM250 + LV432597T + 2x LV432593
Note on M9: Luka Božićević: spare 30% struje
Note on O9: Luka Božićević: spare 30% struje
Note on AM10: Luka Božićević: PSR-ESAM4 48VUC oni koriste ali se ne proizvodi više
Note on E13: Luka Božićević: DODANO 07.04.25.
Note on E14: Luka Božićević: DODANO 07.04.25. izbačen dvosmjeni upravljački izvod i postavljen samo izvod
Note on E15: Luka Božićević: 09.04.2025. dodan izvod
Note on E16: Luka Božićević: 09.04.2025. dodan izvod
Note on E17: Luka Božićević: 09.04.2025. dodan izvod
Note on M21: Luka Božićević: spare 30% struje
Note on O21: Luka Božićević: spare 30% struje
Note on B26: Luka Božićević: 15.07.2025. Dodan novi potrošač -ATEP ga dodatno u PIDu dodao
Note on M28: Luka Božićević: spare 30% struje
Note on O28: Luka Božićević: spare 30% struje
Note on B29: Luka Božićević: NOVO
Note on C29: Luka Božićević: novo 02.2025
Note on M35: Luka Božićević: spare 30% struje
Note on O35: Luka Božićević: spare 30% struje
Note on P35: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517
Note on M42: Luka Božićević: spare 30% struje
Note on O42: Luka Božićević: spare 30% struje
Note on P42: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517
Note on M49: Luka Božićević: spare 30% struje
Note on O49: Luka Božićević: spare 30% struje
Note on P49: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517
Note on F51: Luka Božićević: novi naziv 2mj2026
Note on F53: Luka Božićević: novi naziv 2mj2026
Note on M326: Luka Božićević: spare 30% struje
Note on O326: Luka Božićević: spare 30% struje
Note on P326: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517

## Emerg Boiler MCC distribution
Napomena | Emergency Boiler MCC 4LKF001AR |  |  | BOILER/LOW VOLTAGE CABINET BOILER (EMERGENCY) | CHAUDIÈRE/ARMOIRE BASSE TENSION CHAUDIÈRE (SECOURUE) | [6 empty] | spare 25% -> postavljeno 30% |  |  | 25kA! | 36kA!!!!!!!!!!!!
| Oznaka EPLAN | KKS OLD | KKS prekidača | KKS NEW | KKS NEW - prijevod | PID | 1Ph/3Ph | V | kW | EPLAN kW | kA | Struja motora [A] | Simultaneity factor in maximal normal mode [%] | Struja prekidača s faktorom [A] | Dovodni prekidač SIEMENS | Dovodni prekidač SCHNEIDER | Rastavna sklopka | Reverzibilni | Motorna zaštita Siemens | Motorna zaštita A Siemens | Motorna zaštita AUX Siemens | Sklopnik minimum 12A Siemens | Sklopnik AUX + RC element Siemens | Motorna zaštita Schneider | Motorna zaštita A Schneider | Motorna zaštita A Schneider | 1F Strujni trafo ampermetar | Mjerni strujni trafo za 3F el. Measurement - Socomec | Dozemni spoj - Socomec | Frekventni | Soft starter | Prekidač za 400VAC | Prekidač za 230VAC | Prekidač za 48VAC | RELEJ 48VAC minimum 6A | RELEJ 230VAC minimum 6A | Safety relay | Tip kabela | Strujno opterećenje kabela | vanjski promjer kabela | Proizvođač motora | Klematura | Napomena
| ORMAR 1 2100+200x1000x600 |  | =4LKF001AR+4LKF001AR | [8 empty] | 543.92 |  | 327.8535 | SIE.3KD2832-0NE10-0 (80A) SIE.3KD9103-5 3KD9204-7 (cable cover) | C40F32D400 + LV432597T + 2x LV432593
[16 empty] | INS 400 - SE.31110 29450 (NO/NC) 2xLV432594 (cover) | LV481453 -> ispod ide odvodnik prenapona
|  |  | Predikač prije odvodnika - | [24 empty] | 3x 48290573
Odvodnik prenapona - 5SD7473-1 A9L40321 - Schnider odvodnik prenapona
Nadzor faza - 3UG5514-1BR20
Okretno polje -
| ORMAR 2 2100+200x1000x600 |  | =4LKF001AR+4LKF002AR | [5 empty] | 56.3 | 46.3 |  | 146.731 |  | 131.6965 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | SE.C16F3TM125 - 125A 36kA +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita)
| -F11 | Ash steam vent fan | 4 DEM 071 MO | [4 DEM 071 MO] ASH STEAM VENT FAN | VENTILATEUR DES BUÉES | Ash removal system | 3Ph | 400 | 0.5 | 0.5 | 25 | 0.72 | 100 | 0.72 |  |  |  |  | 3RV2021-1AA10 | 1.1 - 1.6 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P06 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 1 - 1.6 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | RXM4AB2P7 RXZE2S114M RXM021FP | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F12 | Cooling pump 1 | 4 FGR 484 MO | [4 FGR 484 MO] HPU COOLING PUMP | POMPE DE REFROIDISSEMENT HPU | Hydraulic cylinder | 3Ph | 400 | 3 | 3 | 25 | 4.34 | 0 | 0 |  |  |  |  | 3RV2021-1HA10 | 5.5 - 8 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P14 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 6 - 10 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F13 | Cooling fan 1 | 4 FGR 494 ZV | [4 FGR 494 ZV] COOLING FAN 1 | VENTILATEUR DE REFROIDISSEMENT 1 | Hydraulic cylinder | 3Ph | 400 | 0.8 | 0.8 | 25 | 1.16 | 100 | 1.16 |  |  |  |  | 3RV2021-1CA10 | 1.8 - 2.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F14 |  | 4CRF152AR | [4CRF152AR] EMERGENCY COOLER | REFROIDISSEUR D'URGENCE |  | 3Ph | 400 | 19.2 | 19.2 | 25 | 27.75 | 100 | 27.75 | NSX 32A | NG125 - 18727 - 32A +19072 (1CO) | C10F3TM032 - 32A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita) | [9 empty] | 192T2106 CT 60A 192A1204 (0-40A) | 3x 48290501 | 47506015 | [8 empty] | U1000R2V 4G6 |  | 14.3
| -F15 |  | 4CTE111CR | [??] EXPANSION TANK SYSTEM | RÉSERVOIR D'EXPANSION |  | 3Ph | 400 | 10 | 10 | 25 | 14.45 | 50 | 7.225 | NSX 32A | NG125 - 18727 - 32A +19072 (1CO) | C10F3TM032 - 32A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita) | [11 empty] | 47506015 | [8 empty] | U1000R2V 4G2,5 |  | 11.1
| -F16 |  | 4CTE066AR | [4CTE066AR] WATER COOLER 1 | REFROIDISSEUR D'EAU 1 |  | 3Ph | 400 | 6.4 | 6.4 | 25 | 25 | 100 | 25 | NSX 25A | NG125 - 18726 - 25A +19072 (1CO) | C10F3TM025 - 25A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita) | [11 empty] | 47506015 | [8 empty] | U1000R2V 4G4 |  | 12.3
| -F17 |  | 4CTE065AR | [4CTE065AR] WATER COOLER 2 | REFROIDISSEUR D'EAU 2 |  | 3Ph | 400 | 6.4 | 6.4 | 25 | 25 | 100 | 25 | NSX 25A | NG125 - 18726 - 25A +19072 (1CO) | C10F3TM025 - 25A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita) | [11 empty] | 47506015 | [8 empty] | U1000R2V 4G4 |  | 12.3
| -F18 - naknadno dodano na terenu postaviti prekidač | SPARE (prazni prostor) |  | [??] GRATE EXPANSION TANK SYSTEM | SYSTÈME DE RÉSERVOIR D'EXPANSION |  | 3Ph | 400 | 10 | UBACITI U SHEME i naručiti opremu | 25 | 14.45 | 100 | 14.45 |  | NG125 - 18727 - 32A +19072 (1CO) | [21 empty] | U1000R2V 4G2,5 |  | 11.1
| -F19 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 3 2100+200x1000x600 |  | =4LKF001AR+4LKF003AR | [5 empty] | 16.2 | 16.2 |  | 20.111 |  | 20.111 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 - 32A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita)
| -F21 | Cooling pump 2 | 4 FGR 496 MO | [4 FGR 496 MO] HPU EMERGENCY COOLING PUMP | POMPE DE REFROIDISSEMENT D'URGENCE GROUPE HYDRAULIQUE | Hydraulic cylinder | 3Ph | 400 | 7.5 | 7.5 | 25 | 10.84 | 100 | 10.84 |  |  |  |  | 3RV2021-4BA10 | 13 - 20 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2018-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P20 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 13 - 18 A | LC1D18P7 LADN31 (3NO+1NC) LAD4RCU (RC) | 192T2106 CT 60A 192A1202 (0-15A) | 3x 48290500 | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 53 | 11.1
korigiran potrošač 13.07.2026. | -F22 - SPARE | Cooling water pump 1 | SPARE BIO JE: [4 CTE 063 PO] COOLING WATER PUMP 1 | 4 FGO 003 MO LIGHT FUEL OIL PUMP 1 | 4 FGO 003 MO POMPE À FIOUL LÉGER 1 | DOL | 3Ph | 400 | 5.5 | 5.5 | [8 empty] | 3RV2021-1KA10 | 9 - 12.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2017-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP
| -F23 | Drag chain conveyor 1 | 4 DEM 055 MO | [4 DEM 055 MO] DRAG CHAIN CONVEYOR 1 | CONVOYEUR SOUS GRILLE 1 | Ash removal system | 3Ph | 400 | 1.5 | 1.5 | 25 | 2.17 | 100 | 2.17 |  |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC2D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F24 | Sealing air fan 1 | 4 FGR 146 MO | [4 FGR 146 MO] SEALING AIR FAN LEFT | VENTILATEUR D'AIR D'ÉTANCHÉITÉ GAUCHE | Primary air system | 3Ph | 400 | 0.9 | 0.9 | 25 | 1.3 | 100 | 1.3 |  |  |  |  | 3RV2021-1DA10 | 2.2 - 3.2 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F25 | Cooling fan 2 | 4 FGR 493 ZV | [4 FGR 493 ZV] COOLING FAN 2 | VENTILATEUR DE REFROIDISSEMENT 2 | Hydraulic cylinder | 3Ph | 400 | 0.8 | 0.8 | 25 | 1.16 | 100 | 1.16 |  |  |  |  | 3RV2021-1CA10 | 1.8 - 2.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F26 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 4 2100+200x1000x600 |  | =4LKF001AR+4LKF004AR | [5 empty] | 8.7 | 8.7 |  | 16.354 |  | 6.019 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 - 32A +29450 (1CO) +LV429337T (rotary) +LVS04033 (distriblock dole) +LV429517 (duga zaštita)
korigiran potrošač 13.07.2026. | -F31 - SPARE | Cooling water pump 2 | SPARE BIO JE: [4 CTE 064 PO] COOLING WATER PUMP 2 | 4 FGO 004 MO LIGHT FUEL OIL PUMP 2 | 4 FGO 004 MO POMPE À FIOUL LÉGER 2 | DOL | 3Ph | 400 | 5.5 | 5.5 | 25 | 7.95 | 0 | 0 |  |  |  |  | 3RV2021-1KA10 | 9 - 12.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2017-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P16 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 9 - 14 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP
| -F32 | Drag chain conveyor 2 | 4 DEM 066 MO | [4 DEM 066 MO] DRAG CHAIN CONVEYOR 2 | CONVOYEUR SOUS GRILLE 2 | Ash removal system | 3Ph | 400 | 1.5 | 1.5 | 25 | 2.17 | 100 | 2.17 |  |  |  | ☑ | 3RV2021-1FA10 | 3.5 - 5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2016-1AP01 (NO) 3RT2016-1AP01 (NO) 3RA2913-2AA1 (interlock) | 3RT2916-1CD00 (RC) 3RT2936-1CD00 (RC) 3RH2911-1HA31 (aux) 3RH2911-1HA31 (aux) | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC2D12P7 (1NO+1NC) 2x LADN31 (3NO+1NC) 2x LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F33 | Sealing air fan 2 | 4 FGR 160 MO | [4 FGR 160 MO] SEALING AIR FAN RIGHT | VENTILATEUR D'AIR D'ÉTANCHÉITÉ DROIT | Primary air system | 3Ph | 400 | 0.9 | 0.9 | 25 | 1.3 | 100 | 1.3 |  |  |  |  | 3RV2021-1DA10 | 2.2 - 3.2 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F34 | Cooling fan 3 | 4 FGR 492 ZV | [4 FGR 492 ZV] COOLING FAN 3 | VENTILATEUR DE REFROIDISSEMENT 3 | Hydraulic cylinder | 3Ph | 400 | 0.8 | 0.8 | 25 | 1.16 | 100 | 1.16 |  |  |  |  | 3RV2021-1CA10 | 1.8 - 2.5 A | SIE.3RV2901-1E 3RV2901-1A | 3RT2015-1AP02 (1NC) | 3RT2916-1CD00 3RH2911-1HA31 | GV2P08 GVAE11 (NC+NO) GVAD0110 (NC fault + NO) | 2.5 - 4 A | LC1D12P7 (1NO+1NC) LADN31 (3NO+1NC) LAD4RCU (RC) |  |  | 47506015 |  |  |  | A9F74202 | A9F74202 | RXM4AB2E7 RXZE2S114M RXM021BN | LZS:PT5A5T30 LZS:PTMU0730 | XPSBAC34AP | U1000R2V 4G2,5 | 32 | 11.1
| -F35 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| -F36 | SPARE (prazni prostor) |  | SPARE (prazni prostor)
| ORMAR 5 - VFD 2100+200x2000x600 |  | =4LKF001AR+4LKF005AR | [5 empty] | 148 | 148 |  | 278.044 |  | 139.022 |  | SE.C10F3TM100
| -F51 |  | 4 EBA 014 PO | [4 EBA 014 PO] CONDENSATE PUMP 1 | CONDENSATE PUMP 1 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 37 | 37 | 36 | 53.47 | 100 | 53.47 | NSX 63A | C10F3TM063 + LV429515 + LV429515 | 100A PREKIDAČ | [6 empty] | ☑ |  |  |  |  | 47506050 | [8 empty] | NYCWY 3x35/16 2XSLCYK-JB 3x25+3*4
| -F52 |  | 4 CRE 189 MO | [4 CRE 189 MO] COOLING WATER PUMP 1 | POMPE EAU DE REFROIDISSEMENT 1 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 37 | 37 | 36 | 53.47 | 100 | 53.47 | NSX 63A | C10F3TM063 + LV429515 + LV429515 | 100A PREKIDAČ | [6 empty] | ☑ |  |  |  |  | 47506050 | [8 empty] | NYCWY 3x35/16 2XSLCYK-JB 3x25+3*4
| -F53 |  | 4 EBA 043 PO | [4 EBA 043 PO] CONDENSATE PUMP 2 | CONDENSATE PUMP 2 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 37 | 37 | 36 | 53.47 | 0 |  | NSX 63A | C10F3TM063 + LV429515 + LV429515 | 100A PREKIDAČ | [6 empty] | ☑ |  |  |  |  | 47506050 | [8 empty] | NYCWY 3x35/16 2XSLCYK-JB 3x25+3*4
| -F54 |  | 4 CRE 196 MO | [4 CRE 196 MO] COOLING WATER PUMP 2 | COOLING WATER PUMP 2 ALIMENTATION PRINCIPALE | frekventni | 3Ph | 400 | 37 | 37 | 36 | 53.47 | 0 |  | NSX 63A | C10F3TM063 + LV429515 + LV429515 | 100A PREKIDAČ | [6 empty] | ☑ |  |  |  |  | 47506050 | [8 empty] | NYCWY 3x35/16 2XSLCYK-JB 3x25+3*4
| ORMAR 6 - VFD 2100+200x1600x600 ORMAR PRESELJEN S MCC NORMALA |  | =4LKF001AR+4LKF006AR BIO JE:=4LKD001AR+4LKD007AR | [5 empty] | 44 | 11 |  | 82.68 |  | 31.005 | 3VA1032-3ED32-0AA0 - 32A 3VA9988-0AA12 AUX 1CO 3VA9157-0EK11 Rotary 3VA9152-0WA00 phase barrier -> 2 kom 3VA9111-0WD30 mala zaštita odozgora 3VA9113-0JF60 distri odozdola i izolacija | C10F3TM032 + LV429337T + LVS04033 +LV429515
| -F61 - ZAMJENA iz Normala |  | 4SDX 001PO BIO JE: [4 SEO 209 PO] WASTE WATER PUMP 1 | [4 SDX 001 PO] FAST FILING PUMP | POMPE DE REMPLISSAGE RAPIDE | Thermal water treatment | 3Ph | 400 | 11 | AŽURIRAJ samo naziv potrošača | 5 | 15.9 | 0 | 0 | NSX 50A | C10F3TM050 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506030 | [6 empty] | NYCWY 3x6/6
| -F61 - ZAMJENA |  | 4 CTE 063 PO BILO JE: [4 SEO 264 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 1 | [4 CTE 063 PO] COOLING WATER PUMP 1 | POMPE A EAU DE REFROIDISSEMENT 1 | Cooling water | 3Ph | 400 | 5.5 | AŽURIRAJ preimenuj | 25 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015
| -F63 - SPARE |  | SPARE BIO JE: [4 SEO 213 PO] WASTE WATER PUMP 2 | SPARE (popunjen prostor s opremom) |  | frekventni | 3Ph | 400 | 11 | AŽURIRAJ STAVITI SPARE i ostaviti opremu | 5 | 15.9 | 0 | 0 | NSX 50A | C10F3TM050 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506030 | [6 empty] | NYCWY 3x6/6
| -F61 - ZAMJENA |  | 4 CTE 064 PO BILO JE: [4 SEO 269 PO] WASTE WATER BOTTOM ASH PIT DISCHARG PUMP 2 | [4 CTE 064 PO] COOLING WATER PUMP 2 | POMPE A EAU DE REFROIDISSEMENT 2 | Cooling water | 3Ph | 400 | 5.5 | AŽURIRAJ preimenuj | 25 | 7.95 | 0 | 0 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015 | [6 empty] | NYCWY 3x6/6
korigiran potrošač 13.07.2026. | -F65 OSTAJE |  | BIO JE: 4 FGO 003 MO LIGHT FUEL OIL PUMP 1 | SPARE (popunjen prostor s VFD opremom) |  | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015 | [6 empty] | NYCWY 3x6/6
korigiran potrošač 13.07.2026. | -F66 OSTAJE |  | BIO JE: 4 FGO 004 MO LIGHT FUEL OIL PUMP 2 | SPARE (popunjen prostor s VFD opremom) |  | frekventni | 3Ph | 400 | 5.5 | 5.5 | 36 | 7.95 | 100 | 7.95 | NSX 32A | C10F3TM032 + LV429515 + LV429515 | [8 empty] | ☑ | [5 empty] | 47506015 | [6 empty] | NYCWY 3x6/6
| Širina |  | 7600
3x METSECT5CC010 (100/5)
4
Note on M3: Luka Božićević: spare 30% struje
Note on O3: Luka Božićević: spare 30% struje
Note on P3: Luka Božićević: SCHNEIDER: C16B3TM160
Note on M9: Luka Božićević: spare 30% struje
Note on O9: Luka Božićević: spare 30% struje
Note on P9: Luka Božićević: SCHNIDER: C10B3TM063 + LV429337T + LVS04033 +LV429517
Note on M11: Luka Božićević: PROVJERI -> NE SLAŽE SE S COOLING PUMP 2
Note on B17: Luka Božićević: 15.07.2025. dodan novi expansion system za rešetku
Note on M19: Luka Božićević: spare 30% struje
Note on O19: Luka Božićević: spare 30% struje
Note on P19: Luka Božićević: SCHNIDER: C10B3TM063 + LV429337T + LVS04033 +LV429517
Note on F22: Luka Božićević: novi naziv 2mj2026
Note on M26: Luka Božićević: spare 30% struje
Note on O26: Luka Božićević: spare 30% struje
Note on P26: Luka Božićević: SCHNIDER: C10B3TM032 + LV429337T + LVS04033 +LV429517
Note on F28: Luka Božićević: novi naziv 2mj2026
Note on M33: Luka Božićević: spare 30% struje
Note on O33: Luka Božićević: spare 30% struje
Note on P33: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517
Note on M38: Luka Božićević: spare 30% struje
Note on O38: Luka Božićević: spare 30% struje
Note on P38: Luka Božićević: C10B3TM040 + LV429337T + LVS04033 +LV429517
Note on J39: Luka Božićević: 20.08. NOVO STARO BILO 22KW
Note on D43: Luka Božićević: 4 FGO 003 MO POMPE À FIOUL LÉGER 1
Note on AC56: Luka Božićević: ili TCB 26-30

## Stopice i uvodnice
MCC Normal | promjer | količina kabela | Uvodnica Jacob metalna | količina uvodnica | Stopice | količina stopica | količina stopica | Napomena
U1000R2V 4G2,5 | 11.1 | 26 | M20 | 26 | stopica 2,5mm2 | 104 |  | 2 uvodnice po motoru
U1000R2V 4G6 | 14.3 | 1 | M25 | 1 | KSB-C 6/6 | 4
U1000R2V 4G25 | 22.8 | 1 | M40 | 1 | KSB-C 25/6 | 4
MCC Emergency
U1000R2V 4G2,5 | 11.1 | 12 | M20 | 12 | stopica 2,5mm2 | 48
U1000R2V 4G6 | 14.3 | 1 | M25 | 1 | KSB-C 6/6 | 4
U1000R2V 4G4 | 12.3 | 2 | M20 | 2 | stopica 4mm2 | 8
NYCWY 3x35/16 | 32.1 | 0 | M50 | 0 | KSB-C 16/6 | 0 |  | NYCWY 3x35/16 -> 2XSL(St)CYK-J 4G50 (3x50/25)
NYCWY 3x6/6 | 15.6 | 5 | M25 | 5 | KSB-C 6/6 | 20 |  | NYCWY 3x6/6 -> 2XSL(St)CYK-J 4G6 (3x6/6)
Ukupno
|  |  | M20 | 40
|  |  | M25 | 2
|  |  | M40 | 1
Signali - NORD - reducir uvodnica
U1000R2V 5G1,5 | 10.7 | 19 | M20 | 19 | mala stopica | 76 |  | ide u bananu, nije potrebna uvodnica
M32->M20
Naručiti | Narudžbeni broj | Količina | Spare | Ukupno
M32 | 50.632 M | 2 | 20 | 2.4 | 14-20mm
M32x1,5 - reducir | 50.632 M/R | 42 | 30 | 54.6 | 12-20mm
M40 | 50.640 M | 1 | 50 | 1.5
stopica 2,5mm2 |  | 152 | 20 | 182.4
stopica 4mm2 |  | 8 | 20 | 9.6
KSB-C 6/6 | MP 102 002 | 8 | 20 | 9.6
KSB-C 25/6 | MP 102 016 | 4 | 20 | 4.8
Motor koji koristimo | Uvodnica | Stopica
NORD SK3282ABGH-100LP/4 TF -> 100 frame | M32 x2 | M6 | https://nordgearmotors.com/nord-clincher-catalog/#SK3282

## Stopice i uvodnice_rev2
MCC Normal | promjer | količina kabela | Uvodnica Jacob metalna | količina uvodnica | Stopice | količina stopica | količina stopica | Napomena
U1000R2V 4G2,5 | 11.1 | 26 | M20 | 26 | stopica 2,5mm2 | 104 |  | 2 uvodnice po motoru
U1000R2V 4G6 | 14.3 | 1 | M25 | 1 | KSB-C 6/6 | 4
U1000R2V 4G25 | 22.8 | 1 | M40 | 1 | KSB-C 25/6 | 4
MCC Emergency
U1000R2V 4G2,5 | 11.1 | 12 | M20 | 12 | stopica 2,5mm2 | 48
U1000R2V 4G6 | 14.3 | 1 | M25 | 1 | KSB-C 6/6 | 4
U1000R2V 4G4 | 12.3 | 2 | M20 | 2 | stopica 4mm2 | 8
NYCWY 3x35/16 | 32.1 | 0 | M50 | 0 | KSB-C 16/6 | 0 |  | NYCWY 3x35/16 -> 2XSL(St)CYK-J 4G50 (3x50/25)
NYCWY 3x6/6 | 15.6 | 5 | M25 | 5 | KSB-C 6/6 | 20 |  | NYCWY 3x6/6 -> 2XSL(St)CYK-J 4G6 (3x6/6)
Ukupno
|  |  | M20 | 40
|  |  | M25 | 2
|  |  | M40 | 1
Signali - NORD - reducir uvodnica
U1000R2V 5G1,5 | 10.7 | 19 | M20 | 19 | mala stopica | 76 |  | ide u bananu, nije potrebna uvodnica
M32->M20
Naručiti | Narudžbeni broj | Količina | Spare | Ukupno
M32 | 50.632 M | 2 | 20 | 2.4 | 14-20mm
M25 |  | 42 | 20 | 50.4 | 11-16mm
REDUC-M-KV-M32/M25 | 1647637 |  |  | 50.4
M40 | 50.640 M | 1 | 50 | 1.5
stopica 2,5mm2 |  | 152 | 20 | 182.4
stopica 4mm2 |  | 8 | 20 | 9.6
KSB-C 6/6 | MP 102 002 | 8 | 20 | 9.6
KSB-C 25/6 | MP 102 016 | 4 | 20 | 4.8
Motor koji koristimo | Uvodnica | Stopica
NORD SK3282ABGH-100LP/4 TF -> 100 frame | M32 x2 | M6 | https://nordgearmotors.com/nord-clincher-catalog/#SK3282