## Règles
|  | colonne obligatoire ? Mandatory info? | Exemple Example
Depart / Start | Depart du câble Starting point of the cable | x | ARMOIRE TBTF (MCC)
Bornier / Terminal block | Bornier de l'armoire electrique de depart Terminal block of start cabinet | x | X0 - X1 - XDIG - XANA
Borne / Terminal | Borne de l'armoire electrique de depart Terminal of start cabinet | x | -
Repere cable / Cable name | Sigle distinctif du câble NNNN [équipement départ]/AAAA [équipement d'arrivée]-type-xxx [éventuel numéro progressif]. Type du cables: C = câble 24 Vdc B = câble 400Vac, câble 230 Vac M = câble 4÷20mA ou analogique S = câble de données E = eclairage Lettres en majuscules, sans accent Cable name Letters in CAPS | x | TBTF/44FFS220MO-B
Type / Type | Type de câble NOTE 01 = Câble pour les applications à haute température NOTE 02 = Câble fourni avec l'instrument NOTE 03 = Câble blindé et torsadé pour signaux analogique NOTE 04 = Câble blindé par un feuillard/une tresse cuivre pour l'alimentation NOTE 05 = Câble RJ45 FTP cat.6 pour liaisons réseau données NOTE 06 = Multi-mode fiber optic cable avec les characteristics suivant: n°03 couple of conductors, core diameter 62,5/125 micron, connector type ST/SC, armored cable type for rodent protection, the fiber optic cable must be tested by installer NOTE 07 = Câble Profibus pour liaisons réseau données Cable type | x | U1000 RO2V, 2XSLCYK-J, 2YSLCYK-JB, 01IP09EGSF
Formation / Formation | Formation du câble Cable composition | x | -
Longeur / Length | Longueur du câble Cable length | x | -m
Borne / Terminal | Bornes de l'armoire electrique d'arrivee Terminal of arrival cabinet | x | -
Bornier / Terminal block | Bornier de l'armoire electrique d'arrivee Lettres en majuscules, sans accent. Terminal block of arrival cabinet Letters in CAPS | x | -
Arrivee / Arrival | Arrivee du câble Point of arrival of the cable | x | -
Tension/ Voltage | Tension du circuit Voltage circuit | x | 400 Vca, 230 Vca, 48 Vca, 24 Vcc,
Description / Description | Description de l'équipement Description of the function of the cable | x | -

## Cables
Depart | Bornier / Equipement | Borne | Repere cable | Type | Formation | Longeur [m] | Bornier / Equipement | Borne | Arrivee | Tension (V) | Description | Notes | Subsystems | Priority | Obujmice
4CRF180BJ | X | L | 4CRF180BJ/4CRF180HI-B-01 | U1000R2V | 3G1.5 | 10 | X | L | 4CRF180HI | 400Vca | RÉSERVOIR D'EXPANSION À GRILLE |  | Flue gas |  | WCC 14
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4CTE100BJ | X | L | 4CTE100BJ/4CTE100HI-B-01 | U1000R2V | 3G1.5 | 10 | X | L | 4CTE100HI | 400Vca | RÉSERVOIR D'EXPANSION |  | Flue gas |  | WCC 14
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4DCA001CA | X | L1 | 4DCA001CA/4DCA001BC-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA001BC | 230Vca | HVAC UNITÉ EXTÉRIEURE 1 ALIMENTATION |  | HVAC |  | WCC 18
L2
L3
|  | N | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4DCA002CA | X | L1 | 4DCA002CA/4DCA002BC-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA002BC | 230Vca | HVAC UNITÉ EXTÉRIEURE 2 ALIMENTATION |  | HVAC |  | WCC 18
|  | L2 | [12 empty] | #N/A
L3
N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4DCA003CA | X | L1 | 4DCA003CA/4DCA003BC-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA003BC | 230Vca | HVAC UNITÉ EXTÉRIEURE 3 ALIMENTATION |  | HVAC
L2
L3
N
| PE | PE |  |  |  |  | PE | PE
4EAU001BJ | X7 | 1 | 4EAU001BJ/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 215 03 | 13 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION D'ÉCHANTILLONNAGE |  | Chemical dosing station |  | WCC 14
|  | 2 | [5 empty] | 14
| X? | A |  |  |  |  | X 251 03 | 64
|  | A | [5 empty] | 65 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4EPA055VAR | X 033 05 | 22 | 4EPA055VAR/4EPA055CA-C-01 | U1000R2V | 5G1.5 | 80 | X 003 03 | 1 | 4EPA055CA | 48Vca | CONTRÔLE DU POMPE EAU ALIMENTAIRE 1 | 1st floor outside (ground floor) | Thermal water treatment
|  | 23 | [5 empty] | 2 | [6 empty] | #N/A
|  | 27 | [5 empty] | 3
|  | 26 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4EPA055VAR | TA 031 13 | U2 | 4EPA055VAR/4EPA055PO-B-01 | 2XSLCYK-JB EMV-UV | 3x120+3x16 | 80 | M1 | U1 | 4EPA055PO | 400Vca | ALIMENTATION DU POMPE EAU ALIMENTAIRE 1 | 1st floor outside (ground floor) | Thermal water treatment
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1 | [6 empty] | #N/A
|  | PE(1) |  |  |  |  | PE | PE(1)
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3) | [6 empty] | #N/A
4EPA055VAR | TA 031 13 | U2 | 4EPA055VAR/4EPA055PO-B-02 | 2XSLCYK-JB EMV-UV | 3x120+3x16 | 80 | M1 | U1 | 4EPA055PO | 400Vca | ALIMENTATION DU POMPE EAU ALIMENTAIRE 1 | 1st floor outside (ground floor) | Thermal water treatment
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1 | [6 empty] | #N/A
|  | PE(1) |  |  |  |  | PE | PE(1)
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3) | [6 empty] | #N/A
4EPA055VAR | X 053 05 | 4 | 4EPA055VAR/4EPA055PO-M-01 | 08IP09EISF BU | 8x2x0.88 | 80 | BV2 | 1R1 | 4EPA055PO | 24Vcc | SIGNALISATION ANALOGIQUE DU POMPE EAU ALIMENTAIRE 1 | 1st floor outside (ground floor) | Thermal water treatment
|  | 5 | [5 empty] | 1R2
|  | 8 | [5 empty] | 2R1 | [6 empty] | #N/A
|  | 9 | [5 empty] | 2R2
|  | 12 | [5 empty] | 3R1
|  | 13 | [5 empty] | 3R2 | [6 empty] | #N/A
|  | 15 | [5 empty] | 4R1
|  | 16 | [5 empty] | 4R2
|  | 17 | [5 empty] | 4R3 | [6 empty] | #N/A
|  | 19 | [5 empty] | 5R1
|  | 20 | [5 empty] | 5R2
|  | 21 | [5 empty] | 5R3 | [6 empty] | #N/A
|  | 23 | [5 empty] | 1+
|  | 24 | [5 empty] | 2-
|  | 25 | [5 empty] | 1+ | [6 empty] | #N/A
|  | 26 | [5 empty] | 2-
| PE | PE | [5 empty] | PE
4EPA055VAR | X 033 05 | 24 | 4EPA055VAR/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 211 03 | 1 | 4KLD001CQ | 48Vca | CONTRÔLE DU POMPE EAU ALIMENTAIRE 1 | 1st floor | Thermal water treatment |  | WCC 14
|  | 25 | [5 empty] | 2
| X 091 04 | 4 |  |  |  |  | X 251 03 | 2
|  | 5 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4EPA055VAR | X 033 05 | 5 | 4EPA055VAR/4LHA001AR-C-01 | U1000R2V | 3G1.5 | 20 | X 042 14 | 1 | 4LHA001AR | 48Vca | AUTORISATION DE MARCHE DU VFD POMPE EAU ALIMENTAIRE 1 | 1st floor | Thermal water treatment
|  | 21 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4EPA075VAR | X 033 05 | 22 | 4EPA075VAR/4EPA075CA-C-01 | U1000R2V | 5G1.5 | 80 | X 003 03 | 1 | 4EPA075CA | 48Vca | CONTRÔLE DU POMPE EAU ALIMENTAIRE 2 | 1st floor outside (ground floor) | Thermal water treatment
|  | 23 | [5 empty] | 2 | [6 empty] | #N/A
|  | 27 | [5 empty] | 3
|  | 26 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4EPA075VAR | TA 031 13 | U2 | 4EPA075VAR/4EPA075PO-B-01 | 2XSLCYK-JB EMV-UV | 3x120+3x16 | 86 | M1 | U1 | 4EPA075PO | 400Vca | ALIMENTATION DU POMPE EAU ALIMENTAIRE 2 | 1st floor outside (ground floor) | Thermal water treatment
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1 | [6 empty] | #N/A
|  | PE(1) | [5 empty] | PE(1)
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3) | [6 empty] | #N/A
4EPA075VAR | TA 031 13 | U2 | 4EPA075VAR/4EPA075PO-B-02 | 2XSLCYK-JB EMV-UV | 3x120+3x16 | 86 | M1 | U1 | 4EPA075PO | 400Vca | ALIMENTATION DU POMPE EAU ALIMENTAIRE 2 | 1st floor outside (ground floor) | Thermal water treatment
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1 | [6 empty] | #N/A
|  | PE(1) | [5 empty] | PE(1)
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3) | [6 empty] | #N/A
4EPA075VAR | X 053 04 | 4 | 4EPA075VAR/4EPA075PO-M-01 | 08IP09EISF BU | 8x2x0.88 | 86 | X | 1R1 | 4EPA075PO | 24Vcc | SIGNALISATION ANALOGIQUE DU POMPE EAU ALIMENTAIRE 2 | 1st floor outside (ground floor) | Thermal water treatment
|  | 5 | [5 empty] | 1R2
|  | 8 | [5 empty] | 2R1 | [6 empty] | #N/A
|  | 9 | [5 empty] | 2R2
|  | 12 | [5 empty] | 3R1
|  | 13 | [5 empty] | 3R2 | [6 empty] | #N/A
|  | 15 | [5 empty] | 4R1
|  | 16 | [5 empty] | 4R2
|  | 17 | [5 empty] | 4R3 | [6 empty] | #N/A
|  | 19 | [5 empty] | 5R1
|  | 20 | [5 empty] | 5R2
|  | 21 | [5 empty] | 5R3 | [6 empty] | #N/A
|  | 23 | [5 empty] | 1+
|  | 24 | [5 empty] | 2-
|  | 25 | [5 empty] | 1+ | [6 empty] | #N/A
|  | 26 | [5 empty] | 2-
4EPA075VAR | X 033 05 | 24 | 4EPA075VAR/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 215 03 | 9 | 4KLD001CQ | 48Vca | CONTRÔLE DU POMPE EAU ALIMENTAIRE 2 | 1st floor | Thermal water treatment
|  | 25 | [5 empty] | 10 | [6 empty] | #N/A
| X 091 04 | 6 |  |  |  |  | X 251 03 | 17
|  | 7 | [5 empty] | 18
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4EPA075VAR | X 033 05 | 5 | 4EPA075VAR/4LHA001AR-C-01 | U1000R2V | 3G1.5 | 20 | X 043 14 | 1 | 4LHA001AR | 48Vca | AUTORISATION DE MARCHE DU VFD POMPE EAU ALIMENTAIRE 2 | 1st floor | Thermal water treatment
|  | 21 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4ERF203BJ | X2 | 1 | 4ERF203BJ/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 211 03 | 24 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 1 | 1st floor outside (ground floor) | Chemical dosing station
|  | 3 | [5 empty] | 25
|  | 9 | [5 empty] | 26 | [6 empty] | #N/A
|  | 11 | [5 empty] | 27
| PE | PE |  |  |  |  | PE | PE
4ERF223BJ | X2 | 1 | 4ERF223BJ/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 90 | X 211 03 | 36 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 1 | 1st floor outside (ground floor) | Dosage de fosse de neutralisation |  | WCC 14
|  | 3 | [5 empty] | 37
|  | 9 | [5 empty] | 38
|  | 11 | [5 empty] | 39 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4ERF223BJ | X2 | 1 | 4ERF223BJ/4KLD001CQ-C-02 | U1000R2V | 5G1.5 | 90 | X 211 03 | 40 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 2 | 1st floor outside (ground floor) | Dosage de fosse de neutralisation
|  | 3 | [5 empty] | 41 | [6 empty] | #N/A
|  | 9 | [5 empty] | 42
|  | 11 | [5 empty] | 43
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4ERF263BJ | X2 | 1 | 4ERF263BJ/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 90 | X 211 03 | 28 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION DE DOSAGE D'EAU ALIMENTATION 1 | 1st floor outside (ground floor) | Dosage d'eau alimentation
|  | 3 | [5 empty] | 29
|  | 9 | [5 empty] | 30 | [6 empty] | #N/A
|  | 11 | [5 empty] | 31
| PE | PE |  |  |  |  | PE | PE
4ERF263BJ | X2 | 1 | 4ERF263BJ/4KLD001CQ-C-02 | U1000R2V | 5G1.5 | 90 | X 211 03 | 32 | 4KLD001CQ | 24Vcc | CONTRÔLE DU STATION DE DOSAGE D'EAU ALIMENTATION 2 | 1st floor outside (ground floor) | Dosage d'eau alimentation |  | WCC 14
|  | 3 | [5 empty] | 33
|  | 9 | [5 empty] | 34
|  | 11 | [5 empty] | 35 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4FAF065VAR | X 033 05 | 22 | 4FAF065VAR/4FAF065CA-C-01 | U1000R2V | 5G1.5 | 53 | X 003 03 | 1 | 4FAF065CA | 48Vca | CONTRÔLE DU VENTILATEUR D'AIR PRIMAIRE | 1st floor outside (ground floor) | Primary air system
|  | 23 | [5 empty] | 2 | [6 empty] | #N/A
|  | 31 | [5 empty] | 3
|  | 30 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FAF065VAR | X 053 04 | 4 | 4FAF065VAR/4FAF065PO-M-01 | 08IP09EISF BU | 8x2x0.88 | 53 | X | 1R1 | 4FAF065PO | 24Vcc | SIGNALISATION ANALOGIQUE DU VENTILATEUR D'AIR PRIMAIRE | 1st floor outside (ground floor) | Primary air system
|  | 5 | [5 empty] | 1R2
|  | 8 | [5 empty] | 2R1 | [6 empty] | #N/A
|  | 9 | [5 empty] | 2R2
|  | 12 | [5 empty] | 3R1
|  | 13 | [5 empty] | 3R2 | [6 empty] | #N/A
|  | 15 | [5 empty] | 4
|  | 16 | [5 empty] | 6
|  | 17 | [5 empty] | 5 | [6 empty] | #N/A
|  | 19 | [5 empty] | 4
|  | 20 | [5 empty] | 6
|  | 21 | [5 empty] | 5 | [6 empty] | #N/A
|  | 23 | [5 empty] | 1+
|  | 24 | [5 empty] | 2-
|  | 25 | [5 empty] | 1+ | [6 empty] | #N/A
|  | 26 | [5 empty] | 2-
4FAF065VAR | TA 031 12 | U2 | 4FAF065VAR/4FAF065ZV-B-01 | 2XSLCYK-JB EMV-UV | 3x70+3x10 | 53 | M1 | U1 | 4FAF065ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR PRIMAIRE | 1st floor outside (ground floor) | Primary air system
|  | V2 | [5 empty] | V2 | [6 empty] | #N/A
|  | W2 | [5 empty] | W1
|  | PE(1) | [5 empty] | PE(1)
|  | PE(2) | [5 empty] | PE(2) | [6 empty] | #N/A
|  | PE(3) | [5 empty] | PE(3)
4FAF065VAR | TA 031 12 | U2 | 4FAF065VAR/4FAF065ZV-B-02 | 2XSLCYK-JB EMV-UV | 3x70+3x10 | 53 | M1 | U2 | 4FAF065ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR PRIMAIRE | 1st floor outside (ground floor) | Primary air system
|  | V2 | [5 empty] | V2 | [6 empty] | #N/A
|  | W2 | [5 empty] | W2
|  | PE(1) | [5 empty] | PE(1)
|  | PE(2) | [5 empty] | PE(2) | [6 empty] | #N/A
|  | PE(3) | [5 empty] | PE(3)
4FAF065VAR | X 033 05 | 26 | 4FAF065VAR/4FES005MO-C-01 | U1000R2V | 3G1.5 | 53 | X? | ? | 4FES005MO | 24Vcc | AUTORISATION DE MARCHE DU VFD VENTILATEUR D'AIR PRIMAIRE | 1st floor outside (ground floor) | Primary air system
| X 091 04 | 8 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4FAF065VAR | X 071 06 | 1 | 4FAF065VAR/4KLC001AR-C-01 | U1000R2V | 5G1.5 | 20 | X 140 07 | 2 | 4KLC001AR | 24Vcc | SAFE TORQUE OFF DU VFD VENTILATEUR D'AIR PRIMAIRE | 1st to 3rd floor | Primary air system
|  | 2 | [5 empty] | 3 | [6 empty] | #N/A
|  | 4 | [5 empty] | 4
|  | 5 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FAF065VAR | X 033 05 | 28 | 4FAF065VAR/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 211 03 | 5 | 4KLD001CQ | 48Vca | CONTRÔLE DU VENTILATEUR D'AIR PRIMAIRE | 1st floor | Primary air system
|  | 29 | [5 empty] | 6
| X 091 04 | 6 |  |  |  |  | X 251 03 | 7 | [6 empty] | #N/A
|  | 7 | [5 empty] | 8
| PE | PE |  |  |  |  | PE | PE
4FAF065VAR | X 033 05 | 5 | 4FAF065VAR/4LKA001AR-C-01 | U1000R2V | 3G1.5 | 20 | X 043 14 | 1 | 4LKA001AR | 48Vca | AUTORISATION DE MARCHE DU VFD VENTILATEUR D'AIR PRIMAIRE | 1st floor | Primary air system |  | WCC 14
|  | 21 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4FAF065VAR | X 033 05 | 25 | 4FAF065VAR/4LKD002AR-C-01 | U1000R2V | 3G1.5 | 20 | X 111 04 | 5 | 4LKD002AR | 48Vca | SAFETY MATRIX VFD VENTILATEUR D'AIR PRIMAIRE | 1st to 2nd floor | Primary air system |  | WCC 14
|  | 24 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4FGO101CR |  |  | 4FGO101CR/4KCL999CQ-S-01 | IE CABLE |  | 35 | TA 031 11 | P1 | 4KCL999CQ |  | COMUNICATION | 1st to 3rd floor |  |  | #N/A
4FGO101CR |  |  | 4FGO101CR/4KCL999CQ-S-02 | IE CABLE |  | 35 | TA 032 11 | P1 | 4KCL999CQ |  | COMUNICATION | 1st to 3rd floor
4FGR001CA | X | L1 | 4FGR001CA/4FGR001AC-B-01 | U1000R2V | 5G6 | 10 |  |  | 4FGR001AC | 400Vca | ALIMENTATION DU CABINE D'ASCENSEUR (MONTE-CHARGE) |  | Ascenseur
|  | L2 | [12 empty] | #N/A
L2
N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FTA040AR |  |  | 4FTA040AR/4LHA001AR-C-01 | U1000R2V | 3G1.5 | 15 | X 038 14 | 1 | 4LHA001AR | 230Vca | ID FAN (VFD) CB ON | 1st floor | ID fan
2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FTA049VAR | X 033 05 | 22 | 4FTA049VAR/4FTA049CA-C-01 | U1000R2V | 5G1.5 | 28 | X 003 03 | 1 | 4FTA049CA | 48Vca | CONTRÔLE DU VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor outside (ground floor) | Flue gas recirculation system
|  | 23 | [5 empty] | 2
|  | 31 | [5 empty] | 3 | [6 empty] | #N/A
|  | 30 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4FTA049VAR | TA 031 12 | U2 | 4FTA049VAR/4FTA049ZV-B-01 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 28 | M1 | U1 | 4FTA049ZV | 400Vca | ALIMENTATION DU VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor outside (ground floor) | Flue gas recirculation system |  | #N/A
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1
|  | PE(1) | [5 empty] | PE | [6 empty] | #N/A
|  | PE(2) | [5 empty] | PE
|  | PE(3) | [5 empty] | PE
4FTA049VAR | TA 031 12 | U2 | 4FTA049VAR/4FTA049ZV-B-02 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 28 | M1 | U1 | 4FTA049ZV | 400Vca | ALIMENTATION DU VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor outside (ground floor) | Flue gas recirculation system |  | #N/A
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1
|  | PE(1) | [5 empty] | PE | [6 empty] | #N/A
|  | PE(2) | [5 empty] | PE
|  | PE(3) | [5 empty] | PE
4FTA049VAR | X 053 04 | 4 | 4FTA049VAR/4FTA049ZV-M-01 | 08IP09EISF BU | 8x2x0.88 | 28 | X | 1R1 | 4FTA049ZV | 24Vcc | SIGNALISATION ANALOGIQUE DU VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor outside (ground floor) | Flue gas recirculation system |  | #N/A
|  | 5 | [5 empty] | 1R2
|  | 8 | [5 empty] | 2R1
|  | 9 | [5 empty] | 2R2 | [6 empty] | #N/A
|  | 12 | [5 empty] | 3R1
|  | 13 | [5 empty] | 3R2
|  | 15 | [5 empty] | 4R1 | [6 empty] | #N/A
|  | 16 | [5 empty] | 4R2
|  | 17 | [5 empty] | 4R3
|  | 19 | [5 empty] | 5R1 | [6 empty] | #N/A
|  | 20 | [5 empty] | 5R2
|  | 21 | [5 empty] | 5R3
|  | 23 |  |  |  |  | BV1 | 1+ | [6 empty] | #N/A
|  | 24 | [5 empty] | 2-
|  | 25 |  |  |  |  | BV1 | 1+
|  | 26 | [5 empty] | 2- | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4FTA049VAR | X 033 05 | 28 | 4FTA049VAR/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 10 | X 211 03 | 11 | 4KLD001CQ | 48Vca | CONTRÔLE DU VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor | Flue gas recirculation system
|  | 29 | [5 empty] | 12 | [6 empty] | #N/A
| X 091 04 | 6 |  |  |  |  | X 251 03 | 12
|  | 7 | [5 empty] | 13
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FTA049VAR | X 033 05 | 5 | 4FTA049VAR/4LHA001AR-C-01 | U1000R2V | 3G1.5 | 20 | X 041 14 | 1 | 4LHA001AR | 48Vca | AUTORISATION DE MARCHE DU VFD VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor | Flue gas recirculation system
|  | 21 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FTA049VAR | X 033 05 | 26 | 4FTA049VAR/4LKA001AR-C-01 | U1000R2V | 3G1.5 | 20 | X 102 07 | 1 | 4LKA001AR | 48Vca | AUTORISATION DE MARCHE DU VFD VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor | Flue gas recirculation system
| X 091 04 | 8 |  |  |  |  | ? | ?
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4FTA049VAR | X 033 05 | 25 | 4FTA049VAR/4LKF003AR-C-01 | U1000R2V | 3G1.5 | 20 | X 172 11 | 4 | 4LKF003AR | 48Vca | SAFETY MATRIX VFD VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st to 2nd floor | Flue gas recirculation system
|  | 24 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KCL999CQ | TA 031 11 | U2 | 4KCL999CQ/4FGO015ZV-B-01 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 93 | M1 | U1 | 4FGO015ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR DU BRÛLEUR 1 |  | LFO storage tanks
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1 | [6 empty] | #N/A
|  | PE(1) | [5 empty] | PE(1)
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3) | [6 empty] | #N/A
4KCL999CQ | X 057 05 | 4 | 4KCL999CQ/4FGO015ZV-M-01 | 04IP09EISF BU | 4x2x0.88 | 93 | X | 2R1 | 4FGO015ZV | 24Vcc | SIGNALISATION ANALOGIQUE DU VENTILATEUR D'AIR DU BRÛLEUR 1 |  | LFO storage tanks
|  | 5 | [5 empty] | 2R2
| X 091 03 | 1 |  |  |  |  | X? | X? | [6 empty] | #N/A
|  | 2 | [5 empty] | X?
|  | 3 | [5 empty] | X?
|  | 4 | [5 empty] | X? | [6 empty] | #N/A
|  | 5 | [5 empty] | X?
|  | 6 | [5 empty] | X?
4KCL999CQ | TA 032 11 | U2 | 4KCL999CQ/4FGO016ZV-B-01 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 64 | M1 | U1 | 4FGO016ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR DU BRÛLEUR 2 |  | LFO storage tanks |  | #N/A
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1
|  | PE(1) | [5 empty] | PE(1) | [6 empty] | #N/A
|  | PE(2) | [5 empty] | PE(2)
|  | PE(3) | [5 empty] | PE(3)
4KCL999CQ | X 058 05 | 4 | 4KCL999CQ/4FGO016ZV-M-01 | 04IP09EISF BU | 4x2x0.88 | 64 | X | 2R1 | 4FGO016ZV | 24Vcc | SIGNALISATION ANALOGIQUE DU VENTILATEUR D'AIR DU BRÛLEUR 2 |  | LFO storage tanks |  | #N/A
|  | 5 | [5 empty] | 2R2
| X 091 04 | 1 |  |  |  |  | X? | X?
|  | 2 | [5 empty] | X? | [6 empty] | #N/A
|  | 3 | [5 empty] | X?
|  | 4 | [5 empty] | X?
|  | 5 | [5 empty] | X? | [6 empty] | #N/A
|  | 6 | [5 empty] | X?
4KCL999CQ | X 051 03 | 2 | 4KCL999CQ/4FGO101CR-C-01 | U1000R2V | 3G1.5 | 24 | X? | ? | 4FGO101CR | 24Vcc | RÉINITIALISER DU VENTILATEUR D'AIR DU BRÛLEUR 1 | 1st to 3rd floor | LFO storage tanks
|  | 8 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KCL999CQ | X 052 03 | 2 | 4KCL999CQ/4FGO101CR-C-02 | U1000R2V | 3G1.5 | 24 | 25 | ? | 4FGO101CR | 24Vcc | RÉINITIALISER DU VENTILATEUR D'AIR DU BRÛLEUR 2 | 1st to 3rd floor | LFO storage tanks
|  | 8 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KCL999CQ | X 057 05 | 1 | 4KCL999CQ/4FGO101CR-M-01 | 04IP09EISF BU | 4x2x0.88 | 24 | X? | X? | 4FGO101CR | 24Vcc | SIGNALISATION ANALOGIQUE DU VFD VENTILATEUR D'AIR DU BRÛLEUR 1 | 1st to 3rd floor | LFO storage tanks
|  | 2 | [5 empty] | X? | [6 empty] | #N/A
| X 060 09 | 1 | [5 empty] | X?
|  | 2 | [5 empty] | X?
| X 091 03 | 13 | [5 empty] | X? | [6 empty] | #N/A
|  | 14 | [5 empty] | X?
|  | 15 | [5 empty] | X?
|  | 16 | [5 empty] | X? | [6 empty] | #N/A
4KCL999CQ | X 058 05 | 1 | 4KCL999CQ/4FGO101CR-M-02 | 04IP09EISF BU | 4x2x0.88 | 24 | X? | X? | 4FGO101CR | 24Vcc | SIGNALISATION ANALOGIQUE DU VFD VENTILATEUR D'AIR DU BRÛLEUR 2 | 1st to 3rd floor | LFO storage tanks
|  | 2 | [5 empty] | X?
| X 061 09 | 1 | [5 empty] | X? | [6 empty] | #N/A
|  | 2 | [5 empty] | X?
| X 091 04 | 15 | [5 empty] | X?
|  | 16 | [5 empty] | X? | [6 empty] | #N/A
|  | 17 | [5 empty] | X?
|  | 18 | [5 empty] | X?
4KCL999CQ | TA 033 11 | U2 | 4KCL999CQ/4FGR247ZV-B-01 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 35 | M1 | U1 | 4FGR247ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR SECONDAIRE | 1st floor outside (ground floor) | Secondary air system |  | #N/A
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1
|  | PE(2) | [5 empty] | PE | [6 empty] | #N/A
|  | PE(2) | [5 empty] | PE
|  | PE(2) | [5 empty] | PE
4KCL999CQ | TA 033 11 | U2 | 4KCL999CQ/4FGR247ZV-B-02 | 2XSLCYK-JB EMV-UV | 3x50+3x10 | 35 | M1 | U1 | 4FGR247ZV | 400Vca | ALIMENTATION DU VENTILATEUR D'AIR SECONDAIRE | 1st floor outside (ground floor) | Secondary air system |  | #N/A
|  | V2 | [5 empty] | V1
|  | W2 | [5 empty] | W1
|  | PE(2) | [5 empty] | PE | [6 empty] | #N/A
|  | PE(2) | [5 empty] | PE
|  | PE(2) | [5 empty] | PE
4KCL999CQ | X 059 04 | 4 | 4KCL999CQ/4FGR247ZV-M-01 | 04IP09EISF BU | 4x2x0.88 | 35 | X | 1R1 | 4FGR247ZV | 24Vcc | SIGNALISATION ANALOGIQUE DU VENTILATEUR D'AIR SECONDAIRE | 1st floor outside (ground floor) | Secondary air system |  | #N/A
|  | 5 | [5 empty] | 1R2
|  | 8 | [5 empty] | 2R1
|  | 9 | [5 empty] | 2R2 | [6 empty] | #N/A
|  | 12 | [5 empty] | 3R1
|  | 13 | [5 empty] | 3R2
| X 092 03 | 5 |  |  |  |  | X? | ? | [6 empty] | #N/A
|  | 6 | [5 empty] | ?
4KCL999CQ | X 053 03 | 2 | 4KCL999CQ/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 10 | X 211 03 | 9 | 4KLD001CQ | 48Vca | RÉINITIALISER DU VENTILATEUR D'AIR SECONDAIRE | 1st floor | Secondary air system
|  | 8 | [5 empty] | 10 | [6 empty] | #N/A
| X 092 03 | 1 |  |  |  |  | X 251 03 | 4
|  | 2 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KCL999CQ | X 051 03 | 1 | 4KCL999CQ/4LKA001AR-C-01 | U1000R2V | 12G1.5 | 25 | X 055 04 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUES DU VFD VENTILATEUR D'AIR DU BRÛLEUR 1 | 1st floor | Secondary air system
|  | 3 | [5 empty] | 6
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
|  | 7 | [5 empty] | 8
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
| X 091 03 | 7 |  |  |  |  | X 121 04 | 1
|  | 8 | [5 empty] | 2
|  | 9 | [5 empty] | 3 | [6 empty] | #N/A
|  | 10 | [5 empty] | 4
|  | 11 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KCL999CQ | X 052 03 | 1 | 4KCL999CQ/4LKA001AR-C-02 | U1000R2V | 12G1.5 | 25 | X 063 04 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUES DU VFD VENTILATEUR D'AIR DU BRÛLEUR 2 | 1st floor | Secondary air system
|  | 3 | [5 empty] | 6
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
|  | 7 | [5 empty] | 8
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
| X 091 04 | 7 |  |  |  |  | X 121 05 | 1
|  | 8 | [5 empty] | 2
|  | 9 | [5 empty] | 3 | [6 empty] | #N/A
|  | 10 | [5 empty] | 4
|  | 11 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KCL999CQ | X 053 03 | 1 | 4KCL999CQ/4LKA001AR-C-03 | U1000R2V | 12G1.5 | 25 | X 047 04 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUES DU VFD VENTILATEUR D'AIR SECONDAIRE | 1st floor | Secondary air system
|  | 3 | [5 empty] | 6
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
|  | 7 | [5 empty] | 8
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
| X 092 03 | 7 |  |  |  |  | X 121 05 | 6
|  | 8 | [5 empty] | 7
|  | 9 | [5 empty] | 8 | [6 empty] | #N/A
|  | 10 | [5 empty] | 9
|  | 11 | [5 empty] | 10
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KIT003AR | X 041 03 | 1 | 4KIT003AR/4KIT001AR-C-01 | U1000R2V | 3G2.5 | 10 | X 041 03 | 1 | 4KIT001AR | 24Vcc | ALIMENTATION DU PROCESSEUR DE COMMUNICATION DE STATION D'INGÉNIERIE | 3rd floor | LV switchboard
|  | 2 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KIT003AR | X 041 07 | 1 | 4KIT003AR/4KIT001AR-C-02 | U1000R2V | 3G2.5 | 10 | X 041 03 | 3 | 4KIT001AR | 24Vcc | ALIMENTATION DU PROCESSEUR DE COMMUNICATION DE OS SERVEUR 1 | 3rd floor | LV switchboard
|  | 2 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KIT003AR | X 041 10 | 1 | 4KIT003AR/4KIT001AR-C-03 | U1000R2V | 3G2.5 | 10 | X 041 03 | 5 | 4KIT001AR | 24Vcc | ALIMENTATION DU PROCESSEUR DE COMMUNICATION DE OS SERVEUR 2 | 3rd floor | LV switchboard
|  | 2 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KIT003AR | X 241 03 | 1 | 4KIT003AR/4KIT001AR-C-04 | U1000R2V | 5G1.5 | 10 | X 241 02 | 5 | 4KIT001AR | 24Vcc | SIGNALISATION DU SCADA PANEL 1 | 3rd floor | LV switchboard
|  | 2 | [5 empty] | 6
|  | 3 | [5 empty] | 7 | [6 empty] | #N/A
|  | 4 | [5 empty] | 8
| PE | PE |  |  |  |  | PE | PE
4KIT003AR | KF 306 03 | P5 | 4KIT003AR/4KIT001AR-S-01 |  |  | 10 | KF 031 07 | X1 | 4KIT001AR |  | INFORMATION SERVER AND PROCESS HISTORIAN | 3rd floor | LV switchboard |  | #N/A
4KIT003AR | KF 306 03 | P6 | 4KIT003AR/4KIT001AR-S-02 |  |  | 10 | KF 031 02 | X1 | 4KIT001AR |  | OS CLIENT 1 | 3rd floor | LV switchboard
4KIT003AR | KF 306 03 | P8 | 4KIT003AR/4KIT001AR-S-03 |  |  | 10 | KF 031 08 | X1 | 4KIT001AR |  | REDUNDANT DATA SERVERS OS SERVER 1 | 3rd floor | LV switchboard
4KIT003AR | KF 307 03 | P2 | 4KIT003AR/4KIT001AR-S-04 |  |  | 10 | KF 031 04 | X1 | 4KIT001AR |  | OS CLIENT 2 | 3rd floor | LV switchboard |  | #N/A
4KIT003AR | KF 307 03 | P3 | 4KIT003AR/4KIT001AR-S-05 |  |  | 10 | KF 031 05 | X1 | 4KIT001AR |  | ENGINEERING STATION | 3rd floor | LV switchboard
4KIT003AR | KF 307 03 | P4 | 4KIT003AR/4KIT001AR-S-06 |  |  | 10 | KF 031 10 | X1 | 4KIT001AR |  | REDUNDANT DATA SERVERS OS SERVER 2 | 3rd floor | LV switchboard
4KIT003AR | X 241 03 | 1 | 4KIT003AR/4KIT002AR-C-01 | U1000R2V | 5G1.5 | 8 | X 242 02 | 8 | 4KIT002AR | 24Vcc | SIGNALISATION DU SCADA PANEL 2 | 3rd floor | LV switchboard |  | WCC 14
|  | 2 | [5 empty] | 10
|  | 3 | [5 empty] | 9
|  | 4 | [5 empty] | 11 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KIT003AR | KF 306 03 | P4 | 4KIT003AR/4KIT002AR-S-01 |  |  | 8 | KF 031 11 | X1 | 4KIT002AR |  | SALLE PEDAGOGIQUE WORKSTATION | 3rd floor | LV switchboard
4KIT003AR | KF 306 03 | P7 | 4KIT003AR/4KIT002AR-S-02 |  |  | 8 | KF 031 04 | X1 | 4KIT002AR |  | OS CLIENT 4 | 3rd floor | LV switchboard |  | #N/A
4KIT003AR | KF 307 03 | P5 | 4KIT003AR/4KIT002AR-S-03 |  |  | 8 | KF 031 02 | X1 | 4KIT002AR |  | OS CLIENT 3 | 3rd floor | LV switchboard
4KIT003AR | KF 303 03 | P7 | 4KIT003AR/4KIT002AR-S-04 |  |  | 8 | KF 031 10 | X1 | 4KIT002AR |  | REMOVE WORKSTATION | 3rd floor | LV switchboard
4KIT003AR | KF 303 03 | P2 | 4KIT003AR/4KIT002AR-S-05 |  |  | 8 | KF 031 07 | ETH 1 | 4KIT002AR |  | NAS | 3rd floor | LV switchboard |  | #N/A
4KIT003AR | KF 302 03 | P2 | 4KIT003AR/4KIT002AR-S-09 |  |  | 8 | KF 031 08 | X1 P1 | 4KIT002AR |  | DMZ | 3rd floor | LV switchboard
4KIT003AR | KF 306 03 | P2 | 4KIT003AR/CONTROL-S-01 |  |  | 20 | B & W printer A4 | ETH 1 | CONTROL ROOM |  | B & W printer A4 | 3rd to 4th floor
4KIT003AR | KF 306 03 | P3 | 4KIT003AR/CONTROL-S-02 |  |  | 20 | Color printer A3 | ETH 1 | CONTROL ROOM |  | Color printer A3 | 3rd to 4th floor |  |  | #N/A
4KLC001AR | U 326 03 | P4 | 4KLC001AR/4EPA055VAR-S-01 | IE CABLE |  | 35 | TA 031 03 | P1 | 4EPA055VAR |  | COMMUNICATION VFD | 1st to 3rd floor | Thermal water treatment
4KLC001AR | U 325 03 | P2 | 4KLC001AR/4EPA075VAR-S-01 | IE CABLE |  | 35 | TA 031 13 | P1 | 4EPA075VAR |  | COMMUNICATION VFD | 1st to 3rd floor | Thermal water treatment
4KLC001AR | X 211 02 | 25 | 4KLC001AR/4FAF065VAR-C-01 | U1000R2V | 5G1.5 | 40 | X 071 06 | 1 | 4FAF065VAR | 24Vcc | STO DU VFD VENTILATEUR D'AIR PRIMAIRE | 1st to 3rd floor | Primary air system |  | WCC 14
|  | 27 | [5 empty] | 2
|  | 26 | [5 empty] | 4
|  | 28 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | U 325 03 | P6 | 4KLC001AR/4FAF065VAR-S-01 | IE CABLE |  | 33 | TA 031 12 | P1 | 4FAF065VAR |  | COMMUNICATION VFD | 1st to 3rd floor | Primary air system
4KLC001AR | U 287 07 | IN1 | 4KLC001AR/4FES100BC-S-01 | FO |  | 80 |  |  | 4FES100BC |  |  |  | Ash system |  | #N/A
4KLC001AR | U 325 03 | P4 | 4KLC001AR/4FFS325AR-S-01 | IE |  | 20 |  |  | 4FFS325AR |  | ID FAN VFD COMMUNICATION |  | LFO storage tanks
4KLC001AR | X 044 16 | 4 | 4KLC001AR/4FGO101CR-C-01 | U1000R2V | 5G1.5 | 15 | X? | A | 4FGO101CR | 24Vcc |  | 3rd floor | LFO storage tanks
|  | 19 | [5 empty] | A | [6 empty] | #N/A
|  | 5 | [5 empty] | A
|  | 6 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLC001AR | X 211 02 | 21 | 4KLC001AR/4FGO101CR-C-02 | U1000R2V | 5G1.5 | 15 | X? | A | 4FGO101CR | 24Vcc |  | 3rd floor | LFO storage tanks
|  | 23 | [5 empty] | A
|  | 22 | [5 empty] | A | [6 empty] | #N/A
|  | 24 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR |  | ETH | 4KLC001AR/4FGOCR101-S-01 | IE |  | 20 | U 326 03 | P7 | 4FGOCR101 |  | COMMUNICATION |  | LFO storage tanks |  | #N/A
4KLC001AR | X 211 02 | 5 | 4KLC001AR/4FGR001BJ-C-01 | U1000R2V | 5G1.5 | 40 | X? | A | 4FGR001BJ | 24Vcc |  | 3rd floor to outside(ground floor) | Hydraulic cylinder Cylindre hydraulique
|  | 6 |  |  |  |  | X? | A
|  | 7 |  |  |  |  | X? | A | [6 empty] | #N/A
|  | 8 |  |  |  |  | X? | A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | X 211 02 | 29 | 4KLC001AR/4FTA049VAR-C-01 | U1000R2V | 5G1.5 | 40 | X 071 06 | 1 | 4FTA049VAR | 24Vcc | STO DU VFD VENTILATEUR DE RECYCLAGE DES FUMÉES | 1st to 3rd floor | Flue gas recirculation system |  | WCC 14
|  | 30 | [5 empty] | 4
|  | 31 | [5 empty] | 2
|  | 32 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | U322 03 | P6:ETH | 4KLC001AR/4FTA049VAR-S-01 | IE CABLE |  | 20 | TA 031 12 | P1 | 4FTA049VAR |  | COMMUNICATION VFD |  | Fluegas recirculation system
4KLC001AR | U322 03 | P7:ETH | 4KLC001AR/4KCL999CQ-S-01 | IE CABLE |  | 35 | TA 033 11 | P1 | 4KCL999CQ |  | COMMUNICATION VFD |  | Secondary air system |  | #N/A
4KLC001AR | U 323 03 | P1 | 4KLC001AR/4KIT001AR-S-01 | IE CABLE |  | 10 | KF 031 08 | X1 CP1623 | 4KIT001AR |  | COMMUNICATION |  | LV switchboard
4KLC001AR | U 324 03 | P1 | 4KLC001AR/4KIT001AR-S-02 | IE CABLE |  | 10 | KF 031 10 | X1 CP1623 | 4KIT001AR |  | COMMUNICATION |  | LV switchboard
4KLC001AR | U 324 03 | P2 | 4KLC001AR/4KIT001AR-S-03 | IE CABLE |  | 10 |  |  | 4KIT001AR |  | COMMUNICATION |  | LV switchboard |  | #N/A
4KLC001AR | X 211 02 | 37 | 4KLC001AR/4KLC010AR-C-01 | U1000R2V | 27G1.5 | 35 | X? | A | 4KLC010AR | 24Vcc | SIGNALISATION NUMÉRIQUE 4KLC010AR | 3rd floor
|  | 39 | [5 empty] | A
|  | 38 | [5 empty] | A | [6 empty] | #N/A
|  | 40 | [5 empty] | A
|  | 41 | [5 empty] | A
|  | 42 | [5 empty] | A | [6 empty] | #N/A
|  | 43 | [5 empty] | A
|  | 44 | [5 empty] | A
|  | 45 | [5 empty] | A | [6 empty] | #N/A
|  | 46 | [5 empty] | A
|  | 47 | [5 empty] | A
|  | 48 | [5 empty] | A | [6 empty] | #N/A
| X 251 03 | 7 | [5 empty] | A
|  | 8 | [5 empty] | A
|  | 9 | [5 empty] | A | [6 empty] | #N/A
|  | 10 | [5 empty] | A
|  | 11 | [5 empty] | A
|  | 12 | [5 empty] | A | [6 empty] | #N/A
|  | 13 | [5 empty] | A
|  | 14 | [5 empty] | A
|  | 15 | [5 empty] | A | [6 empty] | #N/A
|  | 16 | [5 empty] | A
|  | 17 | [5 empty] | A
|  | 18 | [5 empty] | A | [6 empty] | #N/A
|  | 19 | [5 empty] | A
|  | 20 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLC001AR | U 326 03 | P3 | 4KLC001AR/4KLC010AR-S-01 | IE |  | 35 |  |  | 4KLC010AR |  |  |  | LFO storage tanks
4KLC001AR | X 241 02 | 1 | 4KLC001AR/4KLD001CQ-C-01 | U1000R2V | 12G1.5 | 40 |  |  | 4KLD001CQ | 24Vcc | SIGNALISATION NUMÉRIQUE 4KLC001AR | 1st to 3rd floor | LV switchboard
|  | 3 | [12 empty] | #N/A
4
5
|  | 6 | [12 empty] | #N/A
7
8
|  | 31 | [12 empty] | #N/A
32
33
|  | 34 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | U 326 03 | P6 | 4KLC001AR/4KLD001CQ-S-01 | IE |  | 40 | KF 223 08 | ETH | 4KLD001CQ |  | WEST MODULE COMMUNICATION |  | LV switchboard
4KLC001AR | U 326 03 | P2 | 4KLC001AR/4KLD001CQ-S-02 | IE |  | 40 | KF 224 08 | ETH | 4KLD001CQ |  | WEST MODULE COMMUNICATION |  | LV switchboard |  | #N/A
4KLC001AR | U 326 03 | P5 | 4KLC001AR/4KLD001CQ-S-03 | IE |  | 40 | KF 225 08 | ETH | 4KLD001CQ |  | WEST MODULE COMMUNICATION |  | LV switchboard
4KLC001AR | U 326 03 | P1 | 4KLC001AR/4KLD001CQ-S-04 | IE |  | 40 | KF 226 08 | ETH | 4KLD001CQ |  | WEST MODULE COMMUNICATION |  | LV switchboard
4KLC001AR | KF 309 03 | X1 P2 | 4KLC001AR/4KLD003CQ-S-01 | IE |  | 25 | KF 301 03 | X1: P1 | 4KLD003CQ |  | PLC COMMUNICATION |  | LV switchboard |  | #N/A
4KLC001AR | KF 310 03 | X1 P2 | 4KLC001AR/4KLD003CQ-S-02 | IE |  | 25 | KF 301 03 | X1: P1 | 4KLD003CQ |  | PLC COMMUNICATION |  | LV switchboard
4KLC001AR | X 044 16 | 3 | 4KLC001AR/4LCA201BJ-C-01 | U1000R2V | 5G1.5 | 88 | X 031 03 | 13 | 4LCA201BJ | 24Vcc | SAFETY SIGNALISATION NUMÉRIQUE 4LCA201BJ | 3rd floor to outside
|  | 18 | [5 empty] | 17 | [6 empty] | #N/A
| X 251 03 | 2 |  |  |  |  | X 071 03 | 12
|  | 3 | [5 empty] | 13
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLC001AR | X 113 03 | 1 | 4KLC001AR/4LCA201BJ-M-01 | 04IP09EISF | 4x2x0.88 | 88 | X 051 03 | 9 | 4LCA201BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA201BJ | 3rd floor to outside
|  | 2 | [5 empty] | 12
| X 115 03 | 1 | [5 empty] | 10 | [6 empty] | #N/A
|  | 2 | [5 empty] | 13
| X 117 03 | 1 | [5 empty] | 11
|  | 2 | [5 empty] | 14 | [6 empty] | #N/A
| X 251 03 | 26 |  |  |  |  | X 071 03 | 14
|  | 27 | [5 empty] | 15
4KLC001AR | X 051 03 | 15 | 4KLC001AR/4LCA302BJ-M-01 | 12IP09EGSF BU | 12x2x0.88 | 40 | X 113 03 | 11 | 4LCA302BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA302BJ | 3rd floor to outside |  |  | #N/A
|  | 28 | [5 empty] | 12
|  | 16 | [5 empty] | 13
|  | 29 | [5 empty] | 14 | [6 empty] | #N/A
|  | 17 | [5 empty] | 15
|  | 30 | [5 empty] | 16
|  | 18 |  |  |  |  | X 115 03 | 11 | [6 empty] | #N/A
|  | 31 | [5 empty] | 12
|  | 19 | [5 empty] | 13
|  | 32 | [5 empty] | 14 | [6 empty] | #N/A
|  | 20 | [5 empty] | 15
|  | 33 | [5 empty] | 16
|  | 21 |  |  |  |  | X 117 03 | 11 | [6 empty] | #N/A
|  | 34 | [5 empty] | 12
|  | 22 | [5 empty] | 13
|  | 35 | [5 empty] | 14 | [6 empty] | #N/A
|  | 23 | [5 empty] | 15
|  | 36 | [5 empty] | 16
|  | 24 |  |  |  |  | X 119 03 | 3 | [6 empty] | #N/A
|  | 37 | [5 empty] | 4
|  | 25 | [5 empty] | 5
|  | 38 | [5 empty] | 6 | [6 empty] | #N/A
|  | 26 | [5 empty] | 7
|  | 39 | [5 empty] | 8
4KLC001AR | X 119 03 | 11 | 4KLC001AR/4LCA302BJ-M-02 | 08IP09EISF | 8x2x0.88 | 40 | X 051 03 | 27 | 4LCA302BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA302BJ | 3rd floor to outside |  |  | WCC 26
|  | 12 | [5 empty] | 40
|  | 13 | [5 empty] | 41
|  | 14 | [5 empty] | 45 | [6 empty] | #N/A
|  | 15 | [5 empty] | 42
|  | 16 | [5 empty] | 46
| X 121 03 | 1 | [5 empty] | 43 | [6 empty] | #N/A
|  | 2 | [5 empty] | 47
|  | 3 | [5 empty] | 44
|  | 4 |  |  |  |  | X 071 03 | 48 | [6 empty] | #N/A
| X 251 03 | 38 | [5 empty] | 8
|  | 39 | [5 empty] | 9
|  | 40 | [5 empty] | 10 | [6 empty] | #N/A
|  | 41 | [5 empty] | 11
|  | 42 | [5 empty] | 12
|  | 43 | [5 empty] | 13 | [6 empty] | #N/A
4KLC001AR | X 113 03 | 3 | 4KLC001AR/4LCA701BJ-M-01 | 08IP09EISF | 8x2x0.88 | 82 | X 051 03 | 36 | 4LCA701BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA701BJ | 3rd floor to outside
|  | 4 | [5 empty] | 39
| X 115 03 | 3 | [5 empty] | 37 | [6 empty] | #N/A
|  | 4 | [5 empty] | 40
| X 117 03 | 3 | [5 empty] | 38
|  | 4 | [5 empty] | 41 | [6 empty] | #N/A
| X 119 03 | 1 | [5 empty] | 42
|  | 2 | [5 empty] | 44
|  | 9 | [5 empty] | 43 | [6 empty] | #N/A
|  | 10 | [5 empty] | 45
| X 251 03 | 28 |  |  |  |  | X 071 03 | 14
|  | 29 | [5 empty] | 15 | [6 empty] | #N/A
|  | 30 | [5 empty] | 16
|  | 31 | [5 empty] | 17
|  | 32 | [5 empty] | 18 | [6 empty] | #N/A
|  | 33 | [5 empty] | 19
4KLC001AR | X 113 03 | 7 | 4KLC001AR/4LCA702BJ-M-01 | 04IP09EISF | 4x2x0.88 | 105 | X 051 03 | 65 | 4LCA702BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA702BJ | 3rd floor to outside
|  | 8 | [5 empty] | 68 | [6 empty] | #N/A
| X 115 03 | 7 | [5 empty] | 66
|  | 8 | [5 empty] | 69
| X 117 03 | 7 | [5 empty] | 67 | [6 empty] | #N/A
|  | 8 | [5 empty] | 70
| X 251 03 | 36 |  |  |  |  | X 071 03 | 18
|  | 37 | [5 empty] | 19 | [6 empty] | #N/A
4KLC001AR | X 211 02 | 1 | 4KLC001AR/4LCA801BJ-C-01 | U1000R2V | 5G1.5 | 107 | X 041 03 | 1 | 4LCA801BJ | 24Vcc | SAFETY CONTRÔLE 4LCA702BJ | 3rd floor to outside
|  | 2 | [5 empty] | 5
|  | 3 | [5 empty] | 2 | [6 empty] | #N/A
|  | 4 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | X 113 03 | 5 | 4KLC001AR/4LCA801BJ-M-01 | 08IP09EISF | 8x2x0.88 | 107 | X 051 03 | 1 | 4LCA801BJ | 24Vcc | SAFETY SIGNALISATION ANALOGIQUE 4LCA801BJ | 3rd floor to outside |  |  | WCC 26
|  | 6 | [5 empty] | 4
|  | 9 | [5 empty] | 7
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
| X 115 03 | 5 | [5 empty] | 2
|  | 6 | [5 empty] | 5
|  | 9 | [5 empty] | 8 | [6 empty] | #N/A
|  | 10 | [5 empty] | 11
| X 117 03 | 5 | [5 empty] | 3
|  | 6 | [5 empty] | 6 | [6 empty] | #N/A
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 12
| X 121 03 | 5 |  |  |  |  | X? | A | [6 empty] | #N/A
|  | 6 | [5 empty] | A
| X 251 03 | 34 |  |  |  |  | X 071 03 | 1
|  | 35 | [5 empty] | 2 | [6 empty] | #N/A
4KLC001AR | U 325 03 |  | 4KLC001AR/4LHA001AR-S-01 | ProfiNET - IE FC TP Standard Cable |  | 45 | P 048 13 | DIG 1 | 4LHA001AR |  |  | 1st to 3rd floor | LV switchboard
4KLC001AR | U 326 03 |  | 4KLC001AR/4LHA001AR-S-02 | ProfiNET - IE FC TP Standard Cable |  | 45 | P 048 08 | DIG 1 | 4LHA001AR |  |  | 1st to 3rd floor | LV switchboard
4KLC001AR | X 211 02 | 33 | 4KLC001AR/4LKA001AR-C-01 | U1000R2V | 5G1.5 | 50 | X 211 02 | 34 | 4LKA001AR | 24Vcc |  | 1st to 3rd floor | LV switchboard |  | WCC 14
|  | 35 | [5 empty] | 36
#N/A
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | U 325 03 | P1 | 4KLC001AR/4LKA001AR-S-01 | ProfiNET - IE FC TP Standard Cable |  | 35 | P 084 13 | DIG 1 | 4LKA001AR |  | SOCOMEC D55 COMMUNICATION | 1st to 3rd floor | LV switchboard
4KLC001AR | U 325 03 | P13 | 4KLC001AR/4LKA001AR-S-02 | ProfiNET - IE FC TP Standard Cable |  | 35 | P 084 08 | DIG 1 | 4LKA001AR |  | SOCOMEC D50 COMMUNICATION | 1st to 3rd floor | LV switchboard |  | #N/A
4KLC001AR | U 325 03 | P18 | 4KLC001AR/4LKD001AR-S-01 | IE |  | 15 | P 038 14 | DIG 1 | 4LKD001AR |  | SOCOMEC D50 COMMUNICATION | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 325 03 | P16 | 4KLC001AR/4LKF001AR-S-01 | IE |  | 35 | P 038 14 | DIG 1 | 4LKF001AR |  | SOCOMEC D50 COMMUNICATION | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 325 03 | P14 | 4KLC001AR/4LKF005AR-S-01 | IE |  | 15 | TA 294 08 | ETH | 4LKF005AR |  | COOLING WATER PUMP 2 SFA VFD COMMUNICATION | 2nd to 3rd floor | LV switchboard |  | #N/A
4KLC001AR | U 325 03 | P15 | 4KLC001AR/4LKF005AR-S-02 | IE |  | 15 | TA 293 08 | ETH | 4LKF005AR |  | CONDENSATE PUMP 2 VFD COMMUNICATION | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 326 03 | P21 | 4KLC001AR/4LKF005AR-S-03 | IE |  | 15 | TA 292 08 | ETH | 4LKF005AR |  | COOLING WATER PUMP 1 SFA VFD COMMUNICATION | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 326 03 | P17 | 4KLC001AR/4LKF005AR-S-04 | IE |  | 15 | TA 291 08 | ETH | 4LKF005AR |  | CONDENSATE PUMP 1 VFD COMMUNICATION | 2nd to 3rd floor | LV switchboard |  | #N/A
4KLC001AR | U 325 03 | P21 | 4KLC001AR/4LKF006AR-S-01 | IE |  | 15 |  |  | 4LKF006AR |  |  | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 325 03 | P17 | 4KLC001AR/4LKF006AR-S-02 | IE |  | 15 | TA 514 08 | ETH | 4LKF006AR |  |  | 2nd to 3rd floor | LV switchboard
4KLC001AR | U 326 03 | P8 | 4KLC001AR/4LKF006AR-S-03 | IE |  | 15 | TA 512 08 | ETH | 4LKF006AR |  |  | 2nd to 3rd floor | LV switchboard |  | #N/A
4KLC001AR | U 326 03 | P22 | 4KLC001AR/4LKJ001AR-S-01 | IE |  | 20 |  |  | 4LKJ001AR |  |  | 2nd to 3rd floor | LFO storage tanks
4KLC001AR | U 326 03 | P18 | 4KLC001AR/4LKK001AR-S-01 | IE |  | 17 |  |  | 4LKK001AR |  |  | 1st to 3rd floor | LFO storage tanks
4KLC001AR | U 325 03 | P12 | 4KLC001AR/4LKM001AR-S-01 | IE |  | 10 | P 025 11 | ETH | 4LKM001AR |  |  | 2nd to 3rd floor |  |  | #N/A
4KLC001AR | U 325 03 | P15 | 4KLC001AR/4LMA001AR-S-01 | IE |  | 20 | P 033 03 | ETH | 4LMA001AR |  |  | 2nd to 3rd floor
4KLC001AR | U 287 02 | IN1 | 4KLC001AR/4SAR200BC-S-01 | FO |  | 75 |  |  | 4SAR200BC |  |  |  | Ash system
4KLC001AR |  | ETH | 4KLC001AR/4UPS001LD-S-01 | IE |  | 25 | U 326 03 | P23 | 4UPS001LD |  |  |  | LV switchboard |  | #N/A
4KLC001AR | X 044 16 | 2 | 4KLC001AR/CONTROL ROOM-C-01 | U1000R2V | 5G1.5 | 20 | SF 091 08 | 11 | CONTROL ROOM | 24Vcc | SIGNALISATION NUMÉRIQUE CONTROL ROOM | 3rd to 4th floor
|  | 17 | [5 empty] | 12
|  | 10 | [5 empty] | 21 | [6 empty] | #N/A
|  | 25 | [5 empty] | 22
| PE | PE |  |  |  |  | PE | PE
4KLC001AR | U 287 13 | IN1 | 4KLC001AR/ HV ROOM-S-01 | FO |  | 120 |  |  | HV | [5 empty] | #N/A
4KLC001AR | U 326 03 | P19 | 4KLC001AR/WP3-S-01 | IE |  | 20 |  |  | WP3
4KLD001CQ | X 043 07 | 6 | 4KLD001CQ/4EAU001BJ-C-01 | U1000R2V | 5G1.5 | 75 | X3 | 1 | 4EAU001BJ | 24Vcc |  |  | Sampling station
|  | 29 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 62 |  |  |  |  | X? | A
|  | 63 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 044 05 | 3 | 4KLD001CQ/4EAU001BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 75 | X5 | 1 | 4EAU001BJ | 24Vcc |  |  | Sampling station
|  | 14 | [5 empty] | 2
|  | 4 | [5 empty] | 3 | [6 empty] | #N/A
|  | 15 | [5 empty] | 4
|  | 5 | [5 empty] | 5
|  | 16 | [5 empty] | 6 | [6 empty] | #N/A
|  | 6 | [5 empty] | 7
|  | 17 | [5 empty] | 8
|  | 7 | [5 empty] | 9 | [6 empty] | #N/A
|  | 18 | [5 empty] | 10
|  | 8 | [5 empty] | 11
|  | 19 | [5 empty] | 12 | [6 empty] | #N/A
|  | 9 | [5 empty] | 13
|  | 20 | [5 empty] | 14
| X 044 07 | 2 | [5 empty] | 15 | [6 empty] | #N/A
|  | 12 | [5 empty] | 16
|  | 3 | [5 empty] | 17
|  | 13 | [5 empty] | 18 | [6 empty] | #N/A
|  | 4 | [5 empty] | 19
|  | 14 | [5 empty] | 20
|  | 5 | [5 empty] | 21 | [6 empty] | #N/A
|  | 15 | [5 empty] | 22
|  | 6 | [5 empty] | 23
|  | 16 | [5 empty] | 24 | [6 empty] | #N/A
4KLD001CQ | X 042 16 | 3 | 4KLD001CQ/4EPA055VAR-C-01 | U1000R2V | 7G1.5 | 35 | X 081 05 | 1 | 4EPA055VAR | 24Vcc |  |  | Thermal water treatment
|  | 15 | [5 empty] | 7
|  | 16 | [5 empty] | 6 | [6 empty] | #N/A
| X 211 03 | 3 |  |  |  |  | X 051 04 | 4
|  | 4 | [5 empty] | 7
| X 251 03 | 1 |  |  |  |  | X 091 04 | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 12 | 10 | 4KLD001CQ/4EPA055VAR-M-01 | 08IP09EISF BU | 8x2x0.88 | 35 | X 053 05 | 15 | 4EPA055VAR | 24Vcc |  |  | Thermal water treatment
|  | 11 | [5 empty] | 16 | [6 empty] | #N/A
|  | 12 | [5 empty] | 17
|  | 14 | [5 empty] | 19
|  | 15 | [5 empty] | 20 | [6 empty] | #N/A
|  | 16 | [5 empty] | 21
|  | 3 | [5 empty] | 23
|  | 18 | [5 empty] | 24 | [6 empty] | #N/A
|  | 4 | [5 empty] | 25
|  | 19 | [5 empty] | 26
|  | 20 |  |  |  |  | X 055 09 | 1 | [6 empty] | #N/A
|  | 21 | [5 empty] | 2
| X 132 03 | 1 |  |  |  |  | X 053 04 | 1
|  | 2 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 4 |  |  |  |  | PE | 4
|  | 5 | [5 empty] | 5
4KLD001CQ | X 043 05 | 17 | 4KLD001CQ/4EPA075VAR-C-01 | U1000R2V | 7G1.5 | 35 | X 081 05 | 1 | 4EPA075VAR | 24Vcc |  |  | Thermal water treatment |  | WCC 14
|  | 39 | [5 empty] | 6
|  | 40 | [5 empty] | 7
| X 215 03 | 11 |  |  |  |  | X 051 04 | 7 | [6 empty] | #N/A
|  | 12 | [5 empty] | A
| X 251 03 | 16 |  |  |  |  | X 091 04 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 16 | 21 | 4KLD001CQ/4EPA075VAR-M-01 | 08IP09EISF BU | 8x2x0.88 | 35 | X 053 05 | 15 | 4EPA075VAR | 24Vcc |  |  | Thermal water treatment
|  | 22 | [5 empty] | 16
|  | 23 | [5 empty] | 17 | [6 empty] | #N/A
|  | 25 | [5 empty] | 19
|  | 26 | [5 empty] | 20
|  | 27 | [5 empty] | 21 | [6 empty] | #N/A
|  | 5 | [5 empty] | 23
|  | 29 | [5 empty] | 24
|  | 6 | [5 empty] | 25 | [6 empty] | #N/A
|  | 30 | [5 empty] | 26
| X 044 03 | 11 |  |  |  |  | X 055 09 | 1
|  | 12 | [5 empty] | 2 | [6 empty] | #N/A
| X 133 03 | 1 |  |  |  |  | X 053 04 | 1
|  | 2 | [5 empty] | 2
| X 251 03 | 19 |  |  |  |  | PE | 4 | [6 empty] | #N/A
|  | 20 | [5 empty] | 5
4KLD001CQ | X 043 03 | 5 | 4KLD001CQ/4ERF203BJ-C-01 | U1000R2V | 12G1.5 | 90 | X2 | 5 | 4ERF203BJ | 24Vcc |  |  | Chemical dosing station
|  | 36 | [5 empty] | 6 | [6 empty] | #N/A
|  | 6 | [5 empty] | 7
|  | 37 | [5 empty] | 8
|  | 7 | [5 empty] | 13 | [6 empty] | #N/A
|  | 38 | [5 empty] | 14
|  | 8 | [5 empty] | 15
|  | 39 | [5 empty] | 16 | [6 empty] | #N/A
|  | 9 | [5 empty] | 21
|  | 40 | [5 empty] | 22
|  | 41 | [5 empty] | 23 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 10 | 4KLD001CQ/4ERF203BJ-C-02 | U1000R2V | 5G1.5 | 90 | X2 | 19 | 4ERF203BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE DE CHAUDIÈRE | 1st floor to outside | Chemical dosing station
|  | 42 | [5 empty] | 20 | [6 empty] | #N/A
| X 251 03 | 41 | [5 empty] | A
|  | 42 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 044 03 | 2 | 4KLD001CQ/4ERF203BJ-M-01 | 04IP09EISF BU | 4x2x0.88 | 90 | X2 | 17 | 4ERF203BJ | 24Vcc |  |  | Chemical dosing station
|  | 13 | [5 empty] | 18
| X 133 03 | 3 | [5 empty] | 2 | [6 empty] | #N/A
|  | 4 | [5 empty] | 1
|  | 5 | [5 empty] | 10
|  | 6 | [5 empty] | 9 | [6 empty] | #N/A
| X 251 03 | 43 |  |  |  |  | X? | A
|  | 44 | [5 empty] | A
4KLD001CQ | X 043 03 | 23 | 4KLD001CQ/4ERF223BJ-C-01 | U1000R2V | 12G1.5 | 90 | X2 | 5 | 4ERF223BJ | 24Vcc |  |  | Chemical dosing station |  | #N/A
|  | 57 | [5 empty] | 6
|  | 24 | [5 empty] | 7
|  | 58 | [5 empty] | 8 | [6 empty] | #N/A
|  | 25 | [5 empty] | 13
|  | 59 | [5 empty] | 14
|  | 26 | [5 empty] | 15 | [6 empty] | #N/A
|  | 60 | [5 empty] | 16
|  | 27 | [5 empty] | 21
|  | 61 | [5 empty] | 22 | [6 empty] | #N/A
|  | 62 | [5 empty] | 23
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 28 | 4KLD001CQ/4ERF223BJ-C-02 | U1000R2V | 5G1.5 | 90 | X2 | 19 | 4ERF223BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 1 | 1st floor to outside | Chemical dosing station |  | WCC 14
|  | 63 | [5 empty] | 20
| X 251 03 | 53 | [5 empty] | A
|  | 54 | [5 empty] | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 3 | 4KLD001CQ/4ERF223BJ-C-03 | U1000R2V | 12G1.5 | 90 | X2 | 5 | 4ERF223BJ | 24Vcc | SIGNALISATION ANALOGIQUE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 2 | 1st floor to outside | Chemical dosing station
|  | 23 | [5 empty] | 6 | [6 empty] | #N/A
|  | 4 | [5 empty] | 7
|  | 24 | [5 empty] | 8
|  | 5 | [5 empty] | 13 | [6 empty] | #N/A
|  | 25 | [5 empty] | 14
|  | 6 | [5 empty] | 15
|  | 26 | [5 empty] | 16 | [6 empty] | #N/A
|  | 7 | [5 empty] | 21
|  | 27 | [5 empty] | 22
|  | 28 | [5 empty] | 23 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 8 | 4KLD001CQ/4ERF223BJ-C-04 | U1000R2V | 5G1.5 | 90 | X2 | 19 | 4ERF223BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 2 | 1st floor to outside | Chemical dosing station
|  | 29 | [5 empty] | 20 | [6 empty] | #N/A
| X 251 03 | 57 | [5 empty] | A
|  | 58 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 044 03 | 5 | 4KLD001CQ/4ERF223BJ-M-01 | 04IP09EISF BU | 4x2x0.88 | 90 | X2 | 17 | 4ERF223BJ | 24Vcc |  |  | Chemical dosing station
|  | 16 | [5 empty] | 18
| X 134 03 | 7 | [5 empty] | 2 | [6 empty] | #N/A
|  | 8 | [5 empty] | 1
| X 135 03 | 1 | [5 empty] | 10
|  | 2 | [5 empty] | 9 | [6 empty] | #N/A
| X 251 03 | 55 |  |  |  |  | X? | A
|  | 56 | [5 empty] | A
4KLD001CQ | X 044 03 | 6 | 4KLD001CQ/4ERF223BJ-M-02 | 04IP09EISF | 4x2x0.88 | 90 | X2 | 17 | 4ERF223BJ | 24Vcc | SIGNALISATION ANALOGIQUE DU STATION DE DOSAGE DE FOSSE DE NEUTRALISATION 2 | 1st floor to outside | Chemical dosing station |  | WCC 18
|  | 17 | [5 empty] | 18
| X 135 03 | 3 | [5 empty] | 2
|  | 4 | [5 empty] | 1 | [6 empty] | #N/A
|  | 5 | [5 empty] | 10
|  | 6 | [5 empty] | 9
| X 251 03 | 59 |  |  |  |  | PE | PE | [6 empty] | #N/A
60
4KLD001CQ | X 043 03 | 11 | 4KLD001CQ/4ERF263BJ-C-01 | U1000R2V | 12G1.5 | 90 | X2 | 5 | 4ERF263BJ | 24Vcc |  |  | Chemical dosing station
|  | 43 | [5 empty] | 6 | [6 empty] | #N/A
|  | 12 | [5 empty] | 7
|  | 44 | [5 empty] | 8
|  | 13 | [5 empty] | 13 | [6 empty] | #N/A
|  | 45 | [5 empty] | 14
|  | 14 | [5 empty] | 15
|  | 46 | [5 empty] | 16 | [6 empty] | #N/A
|  | 15 | [5 empty] | 21
|  | 47 | [5 empty] | 22
|  | 48 | [5 empty] | 23 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 03 | 16 | 4KLD001CQ/4ERF263BJ-C-02 | U1000R2V | 5G1.5 | 90 | X2 | 19 | 4ERF263BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE D'EAU ALIMENTATION 1 | 1st floor to outside | Chemical dosing station
|  | 49 | [5 empty] | 20 | [6 empty] | #N/A
| X 251 03 | 45 | [5 empty] | A
|  | 46 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 03 | 17 | 4KLD001CQ/4ERF263BJ-C-03 | U1000R2V | 12G1.5 | 90 | X2 | 5 | 4ERF263BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE D'EAU ALIMENTATION 2 | 1st floor to outside | Chemical dosing station
|  | 50 | [5 empty] | 6
|  | 18 | [5 empty] | 7 | [6 empty] | #N/A
|  | 51 | [5 empty] | 8
|  | 19 | [5 empty] | 13
|  | 52 | [5 empty] | 14 | [6 empty] | #N/A
|  | 20 | [5 empty] | 15
|  | 53 | [5 empty] | 16
|  | 21 | [5 empty] | 21 | [6 empty] | #N/A
|  | 54 | [5 empty] | 22
|  | 55 | [5 empty] | 23
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 03 | 22 | 4KLD001CQ/4ERF263BJ-C-04 | U1000R2V | 5G1.5 | 90 | X2 | 19 | 4ERF263BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU STATION DE DOSAGE D'EAU ALIMENTATION 2 | 1st floor to outside | Chemical dosing station
|  | 56 | [5 empty] | 20
| X 251 03 | 49 | [5 empty] | A | [6 empty] | #N/A
|  | 50 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 044 03 | 3 | 4KLD001CQ/4ERF263BJ-M-01 | 04IP09EISF BU | 4x2x0.88 | 90 | X2 | 17 | 4ERF263BJ | 24Vcc |  |  | Chemical dosing station |  | #N/A
|  | 14 | [5 empty] | 18
| X 133 03 | 7 | [5 empty] | 2
|  | 8 | [5 empty] | 1 | [6 empty] | #N/A
| X 134 03 | 1 | [5 empty] | 10
|  | 2 | [5 empty] | 9
| X 251 03 | 47 |  |  |  |  | X? | A | [6 empty] | #N/A
|  | 48 | [5 empty] | A
4KLD001CQ | X 044 03 | 4 | 4KLD001CQ/4ERF263BJ-M-02 | 04IP09EISF | 4x2x0.88 | 90 | X2 | 17 | 4ERF263BJ | 24Vcc | SIGNALISATION ANALOGIQUE DU STATION DE DOSAGE D'EAU ALIMENTATION 2 | 1st floor to outside | Chemical dosing station
|  | 15 | [5 empty] | 18 | [6 empty] | #N/A
| X 134 04 | 3 | [5 empty] | 2
|  | 4 | [5 empty] | 1
|  | 5 | [5 empty] | 10 | [6 empty] | #N/A
|  | 6 | [5 empty] | 9
| X 251 03 | 51 | [5 empty] | A
|  | 52 | [5 empty] | A | [6 empty] | #N/A
4KLD001CQ | X 042 16 | 4 | 4KLD001CQ/4FAF065VAR-C-01 | U1000R2V | 7G1.5 | 33 | X 081 05 | 1 | 4FAF065VAR | 24Vcc |  |  | Primary air system
|  | 17 | [5 empty] | 7
|  | 18 | [5 empty] | 6 | [6 empty] | #N/A
| X 211 03 | 7 |  |  |  |  | X 051 04 | 4
|  | 8 | [5 empty] | 7
| X 251 03 | 6 |  |  |  |  | X 091 04 | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 12 | 22 | 4KLD001CQ/4FAF065VAR-M-01 | 08IP09EISF BU | 8x2x0.88 | 33 | X 053 03 | 15 | 4FAF065VAR | 24Vcc |  |  | Primary air system
|  | 23 | [5 empty] | 16 | [6 empty] | #N/A
|  | 24 | [5 empty] | 17
|  | 26 | [5 empty] | 19
|  | 27 | [5 empty] | 20 | [6 empty] | #N/A
|  | 28 | [5 empty] | 21
|  | 6 | [5 empty] | 23
|  | 30 | [5 empty] | 24 | [6 empty] | #N/A
| X 043 14 | 2 | [5 empty] | 25
|  | 10 | [5 empty] | 26
|  | 11 |  |  |  |  | X 055 09 | 1 | [6 empty] | #N/A
|  | 12 | [5 empty] | 2
| X 132 03 | 3 |  |  |  |  | X 053 04 | 1
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 9 |  |  |  |  | PE | 4
|  | 10 | [5 empty] | 5
4KLD001CQ | X 043 05 | 9 | 4KLD001CQ/4FGR001BJ-C-01 | U1000R2V | 12G1.5 | 33 | X1 | 10 | 4FGR001BJ | 24Vcc |  | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | #N/A
|  | 30 | [5 empty] | 11
|  | 10 | [5 empty] | 13
|  | 31 | [5 empty] | 14 | [6 empty] | #N/A
|  | 11 | [5 empty] | 16
|  | 32 | [5 empty] | 17
|  | 12 | [5 empty] | 7 | [6 empty] | #N/A
|  | 33 | [5 empty] | 8
|  | 13 | [5 empty] | 6
|  | 34 | [5 empty] | 5 | [6 empty] | #N/A
| X 251 03 | 66 |  |  |  |  | X? | A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 14 | 4KLD001CQ/4FGR001BJ-C-02 | U1000R2V | 5G1.5 | 33 | X1 | 4 | 4FGR001BJ | 24Vcc | SIGNALISATION NUMÉRIQUE DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | WCC 14
|  | 35 | [5 empty] | 3
|  | 15 | [5 empty] | 2
|  | 36 | [5 empty] | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 03 | 14 | 4KLD001CQ/4FGR001BJ-C-03 | U1000R2V | 27G1.5 | 33 | X1 | 33 | 4FGR001BJ | 24Vcc | CONTRÔLE DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 4 | [5 empty] | 34 | [6 empty] | #N/A
|  | 15 | [5 empty] | 47
|  | 5 | [5 empty] | 48
|  | 16 | [5 empty] | 61 | [6 empty] | #N/A
|  | 6 | [5 empty] | 62
|  | 17 | [5 empty] | 163
|  | 7 | [5 empty] | 164 | [6 empty] | #N/A
|  | 18 | [5 empty] | 165
|  | 8 | [5 empty] | 166
|  | 19 | [5 empty] | 167 | [6 empty] | #N/A
|  | 9 | [5 empty] | 168
|  | 20 | [5 empty] | 169
|  | 10 | [5 empty] | 170 | [6 empty] | #N/A
|  | 21 | [5 empty] | 171
|  | 11 | [5 empty] | 172
|  | 22 | [5 empty] | 173 | [6 empty] | #N/A
|  | 12 | [5 empty] | 174
|  | 23 | [5 empty] | 175
|  | 13 | [5 empty] | 176 | [6 empty] | #N/A
| X 045 05 | 18 | [5 empty] | 177
|  | 8 | [5 empty] | 178
| X 251 03 | 67 |  |  |  |  | X? | A | [6 empty] | #N/A
|  | 68 | [5 empty] | A
|  | 69 | [5 empty] | A
|  | 70 | [5 empty] | A | [6 empty] | #N/A
| PE | PE | [5 empty] | PE
4KLD001CQ | X 046 03 | 2 | 4KLD001CQ/4FGR001BJ-C-04 | U1000R2V | 4G2.5 | 33 | X1 | 21 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE PROPORTIONNELLE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 6 | [5 empty] | 22 | [6 empty] | #N/A
|  | 7 | [5 empty] | 23
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 046 03 | 3 | 4KLD001CQ/4FGR001BJ-C-05 | U1000R2V | 4G2.5 | 33 | X1 | 35 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE PROPORTIONNELLE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | WCC 14
|  | 8 | [5 empty] | 36
|  | 9 | [5 empty] | 37
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 046 03 | 4 | 4KLD001CQ/4FGR001BJ-C-06 | U1000R2V | 4G2.5 | 33 | X1 | 49 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE PROPORTIONNELLE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 10 | [5 empty] | 50
|  | 11 | [5 empty] | 51 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 09 | 3 | 4KLD001CQ/4FGR001BJ-C-07 | U1000R2V | 4G2.5 | 33 | X1 | 67 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 9 | [5 empty] | 68 | [6 empty] | #N/A
|  | 10 | [5 empty] | 69
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 09 | 4 | 4KLD001CQ/4FGR001BJ-C-08 | U1000R2V | 4G2.5 | 33 | X1 | 115 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | WCC 14
|  | 11 | [5 empty] | 116
|  | 12 | [5 empty] | 117
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 045 12 | 3 | 4KLD001CQ/4FGR001BJ-C-09 | U1000R2V | 4G2.5 | 33 | X1 | 79 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 9 | [5 empty] | 80
|  | 10 | [5 empty] | 81 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 12 | 4 | 4KLD001CQ/4FGR001BJ-C-10 | U1000R2V | 4G2.5 | 33 | X1 | 127 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 11 | [5 empty] | 128 | [6 empty] | #N/A
|  | 12 | [5 empty] | 129
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 14 | 3 | 4KLD001CQ/4FGR001BJ-C-11 | U1000R2V | 4G2.5 | 33 | X1 | 91 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | WCC 14
|  | 9 | [5 empty] | 92
|  | 10 | [5 empty] | 93
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 045 14 | 4 | 4KLD001CQ/4FGR001BJ-C-12 | U1000R2V | 4G2.5 | 33 | X1 | 139 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 11 | [5 empty] | 140
|  | 12 | [5 empty] | 141 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 16 | 3 | 4KLD001CQ/4FGR001BJ-C-13 | U1000R2V | 4G2.5 | 33 | X1 | 103 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 9 | [5 empty] | 104 | [6 empty] | #N/A
|  | 10 | [5 empty] | 105
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 16 | 4 | 4KLD001CQ/4FGR001BJ-C-14 | U1000R2V | 4G2.5 | 33 | X1 | 151 | 4FGR001BJ | 24Vcc | ALIMENTATION DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE VANNE D'IMPULSION | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique |  | WCC 14
|  | 11 | [5 empty] | 152
|  | 12 | [5 empty] | 153
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 044 03 | 7 | 4KLD001CQ/4FGR001BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 33 | X1 | 179 | 4FGR001BJ | 24Vcc | SIGNALISATION ANALOGIQUE DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 18 | [5 empty] | 180
|  | 19 | [5 empty] | 182 | [6 empty] | #N/A
| X 044 05 | 2 | [5 empty] | 19
|  | 13 | [5 empty] | 20
| X 135 03 | 7 | [5 empty] | 24 | [6 empty] | #N/A
|  | 8 | [5 empty] | 25
| X 136 03 | 1 | [5 empty] | 38
|  | 2 | [5 empty] | 39 | [6 empty] | #N/A
|  | 3 | [5 empty] | 52
|  | 4 | [5 empty] | 53
| X 223 13 | 1 | [5 empty] | 70 | [6 empty] | #N/A
|  | 2 | [5 empty] | 71
|  | 3 | [5 empty] | 118
|  | 4 | [5 empty] | 119 | [6 empty] | #N/A
| X 251 03 | 71 |  |  |  |  | X? | A
4KLD001CQ | X 223 13 | 5 | 4KLD001CQ/4FGR001BJ-M-02 | 08IP09EISF | 8x2x0.88 | 33 | X1 | 82 | 4FGR001BJ | 24Vcc | SIGNALISATION ANALOGIQUE DU BOÎTE DE JONCTION GROUPE HYDRAULIQUE | 1st floor to outside | Hydraulic cylinder Cylindre hydraulique
|  | 6 | [5 empty] | 83 | [6 empty] | #N/A
|  | 7 | [5 empty] | 130
|  | 8 | [5 empty] | 131
|  | 9 | [5 empty] | 94 | [6 empty] | #N/A
|  | 10 | [5 empty] | 95
|  | 11 | [5 empty] | 142
|  | 12 | [5 empty] | 143 | [6 empty] | #N/A
|  | 13 | [5 empty] | 106
|  | 14 | [5 empty] | 107
|  | 15 | [5 empty] | 154 | [6 empty] | #N/A
|  | 16 | [5 empty] | 155
| X 251 03 | 72 | [5 empty] | A
|  | 73 | [5 empty] | A | [6 empty] | #N/A
|  | 74 | [5 empty] | A
|  | 75 | [5 empty] | A
4KLD001CQ | X 042 16 | 5 | 4KLD001CQ/4FTA049VAR-C-01 | U1000R2V | 7G1.5 | 20 | X 081 05 | 1 | 4FTA049VAR | 24Vcc |  |  | Fluegas recirculation system |  | WCC 14
|  | 19 | [5 empty] | 7
|  | 20 | [5 empty] | 6
| X 211 03 | 13 |  |  |  |  | X 051 04 | 4 | [6 empty] | #N/A
|  | 14 | [5 empty] | 7
| X 251 03 | 11 |  |  |  |  | X 091 04 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 14 | 6 | 4KLD001CQ/4FTA049VAR-M-01 | 08IP09EISF BU | 8x2x0.88 | 20 | X 053 05 | 23 | 4FTA049VAR | 24Vcc |  |  | Fluegas recirculation system
|  | 25 | [5 empty] | 24
| X 043 16 | 2 | [5 empty] | 25 | [6 empty] | #N/A
|  | 10 | [5 empty] | 26
|  | 11 | [5 empty] | 15
|  | 12 | [5 empty] | 16 | [6 empty] | #N/A
|  | 13 | [5 empty] | 17
|  | 15 | [5 empty] | 19
|  | 16 | [5 empty] | 20 | [6 empty] | #N/A
|  | 17 | [5 empty] | 21
|  | 19 |  |  |  |  | X 59 05 | 1
|  | 20 | [5 empty] | 2 | [6 empty] | #N/A
| X 132 03 | 7 |  |  |  |  | X 053 04 | 1
|  | 8 | [5 empty] | 2
| X 251 03 | 14 |  |  |  |  | PE | 4 | [6 empty] | #N/A
|  | 15 | [5 empty] | 5
4KLD001CQ | X 043 14 | 13 | 4KLD001CQ/4KCL999CQ-M-01 | 08IP09EISF BU | 8x2x0.88 | 35 | X? | A | 4KCL999CQ | 24Vcc |  |  | Secondary air system
|  | 14 | [5 empty] | A | [6 empty] | #N/A
|  | 15 | [5 empty] | A
|  | 17 | [5 empty] | A
|  | 18 | [5 empty] | A | [6 empty] | #N/A
|  | 19 | [5 empty] | A
|  | 4 | [5 empty] | A
|  | 21 | [5 empty] | A | [6 empty] | #N/A
|  | 5 | [5 empty] | A
|  | 22 | [5 empty] | A
|  | 23 |  |  |  |  | X 062 09 | 1 | [6 empty] | #N/A
|  | 24 | [5 empty] | 2
| X 132 03 | 5 |  |  |  |  | X 059 04 | 1
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 23 |  |  |  |  | X? | A
|  | 24 | [5 empty] | A
4KLD001CQ | KF 301 03 | -X1 P2 | 4KLD001CQ/4KLD006CQ-S-01 | Fiber optic |  | 25 | KF 301 03 | -X1 P1 | 4KLD006CQ | 24Vcc |  |  | Flue gas |  | #N/A
4KLD001CQ | KF 302 03 | -X1 P2 | 4KLD001CQ/4KLD006CQ-S-02 | Fiber optic |  | 25 | KF 302 03 | -X1 P1 | 4KLD006CQ | 24Vcc |  |  | Flue gas
4KLD001CQ | X 043 07 | 7 | 4KLD001CQ/4LCA001CR-C-01 | U1000R2V | 12G1.5 | 10 | X 030 02 | 1 | 4LCA001CR | 24Vcc |  |  | Thermal water treatment
|  | 34 | [5 empty] | 4 | [6 empty] | #N/A
|  | 35 | [5 empty] | 5
|  | 36 | [5 empty] | 6
|  | 37 | [5 empty] | 7 | [6 empty] | #N/A
|  | 38 | [5 empty] | 8
|  | 39 | [5 empty] | 9
|  | 40 | [5 empty] | 10 | [6 empty] | #N/A
|  | 41 | [5 empty] | 11
|  | 42 | [5 empty] | 12
| X 251 03 | 76 |  |  |  |  | X? | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | X? | PE
4KLD001CQ | X 043 07 | 43 | 4KLD001CQ/4LCA001CR-C-02 | U1000R2V | 5G1.5 | 10 | X 030 02 | 13 | 4LCA001CR | 24Vcc |  | 1st floor
|  | 44 | [5 empty] | 14 | [6 empty] | #N/A
|  | 45 | [5 empty] | 15
| X 251 03 | 77 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 044 07 | 7 | 4KLD001CQ/4LCA101BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 47 | X 051 03 | 1 | 4LCA101BJ | 24Vcc |  |  | Hydraulic cylinder
|  | 17 | [5 empty] | 4
|  | 18 | [5 empty] | 5 | [6 empty] | #N/A
|  | 19 | [5 empty] | 6
| X 044 09 | 2 | [5 empty] | 7
|  | 9 | [5 empty] | 9 | [6 empty] | #N/A
|  | 10 | [5 empty] | 10
| X 251 03 | 78 |  |  |  |  | X 071 03 | 10
|  | 79 | [5 empty] | 11 | [6 empty] | #N/A
|  | 80 | [5 empty] | 12
|  | 81 | [5 empty] | 13
|  | 82 | [5 empty] | 14 | [6 empty] | #N/A
|  | 83 | [5 empty] | 15
|  | 84 | [5 empty] | 16
|  | 85 | [5 empty] | 17 | [6 empty] | #N/A
|  | 86 | [5 empty] | 18
4KLD001CQ | X 044 09 | 3 | 4KLD001CQ/4LCA102BJ-M-01 | 04IP09EISF BU | 4x2x0.88 | 75 | X 051 03 | 25 | 4LCA102BJ | 24Vcc |  |  | Pneumatic rapping system
|  | 11 | [5 empty] | 28 | [6 empty] | #N/A
|  | 12 | [5 empty] | 29
|  | 13 | [5 empty] | 30
| X 251 03 | 87 |  |  |  |  | X 071 03 | 12 | [6 empty] | #N/A
|  | 88 | [5 empty] | 13
|  | 89 | [5 empty] | 14
|  | 90 | [5 empty] | 15 | [6 empty] | #N/A
4KLD001CQ | X 045 09 | 5 | 4KLD001CQ/4LCA203BJ-C-01 | U1000R2V | 4G2.5 | 50 | X 055 02 | 1 | 4LCA203BJ | 24Vcc |  |  | Primary air system
|  | 13 | [5 empty] | 3
|  | 14 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 12 | 5 | 4KLD001CQ/4LCA203BJ-C-02 | U1000R2V | 4G2.5 | 50 | X 055 02 | 7 | 4LCA203BJ | 24Vcc |  | 1st floor to outside
|  | 13 | [5 empty] | 9 | [6 empty] | #N/A
|  | 14 | [5 empty] | 11
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 14 | 5 | 4KLD001CQ/4LCA203BJ-C-03 | U1000R2V | 4G2.5 | 50 | X 055 02 | 13 | 4LCA203BJ | 24Vcc |  | 1st floor to outside |  |  | WCC 14
|  | 13 | [5 empty] | 15
|  | 14 | [5 empty] | 17
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 045 16 | 5 | 4KLD001CQ/4LCA203BJ-C-04 | U1000R2V | 4G2.5 | 50 | X 055 02 | 19 | 4LCA203BJ | 24Vcc |  | 1st floor to outside
|  | 13 | [5 empty] | 21
|  | 14 | [5 empty] | 23 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 045 09 | 17 | 4KLD001CQ/4LCA203BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 50 | X 051 03 | 33 | 4LCA203BJ | 24Vcc |  |  | Primary air system
|  | 18 | [5 empty] | 41 | [6 empty] | #N/A
|  | 20 | [5 empty] | 34
|  | 19 | [5 empty] | 42
| X 045 12 | 17 | [5 empty] | 35 | [6 empty] | #N/A
|  | 18 | [5 empty] | 43
|  | 20 | [5 empty] | 36
|  | 19 | [5 empty] | 44 | [6 empty] | #N/A
| X 045 14 | 17 | [5 empty] | 37
|  | 18 | [5 empty] | 45
|  | 20 | [5 empty] | 38 | [6 empty] | #N/A
|  | 19 | [5 empty] | 46
| X 045 16 | 17 | [5 empty] | 39
|  | 18 | [5 empty] | 47 | [6 empty] | #N/A
|  | 20 | [5 empty] | 40
|  | 19 | [5 empty] | 48
4KLD001CQ | X 043 05 | 18 | 4KLD001CQ/4LHA001AR-C-01 | U1000R2V | 12G1.5 | 55 | X 031 09 | 1 | 4LHA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LHA001AR | 1st floor |  |  | #N/A
|  | 41 | [5 empty] | 8
|  | 42 | [5 empty] | 9
|  | 43 | [5 empty] | 10 | [6 empty] | #N/A
|  | 44 | [5 empty] | 11
|  | 45 | [5 empty] | 12
|  | 46 | [5 empty] | 13 | [6 empty] | #N/A
|  | 47 | [5 empty] | 14
|  | 48 | [5 empty] | 15
[8 empty] | 16 | [6 empty] | #N/A
17
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 49 | 4KLD001CQ/4LHA001AR-C-02 | U1000R2V | 7G1.5 | 55 | X 031 09 | 18 | 4LHA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LHA001AR | 1st floor |  |  | WCC 14
|  | 50 | [5 empty] | 19
|  | 51 | [5 empty] | 20
|  | 52 | [5 empty] | 20 | [6 empty] | #N/A
53
| X 251 03 | 35
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 05 | 19 | 4KLD001CQ/4LHA001AR-C-03 | U1000R2V | 12G1.5 | 55 | X 092 03 | 1 | 4LHA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LHA001AR | 1st floor
|  | 54 | [5 empty] | 3
| X 043 07 | 3 | [5 empty] | 4 | [6 empty] | #N/A
|  | 15 | [5 empty] | 5
|  | 16 | [5 empty] | 6
|  | 17 | [5 empty] | 7 | [6 empty] | #N/A
| X 251 03 | 18 | [5 empty] | 8
|  | 36 |  |  |  |  | X? | A
|  | 37 | [5 empty] | A | [6 empty] | #N/A
|  | 38 | [5 empty] | A
|  | 39 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 07 | 4 | 4KLD001CQ/4LHA001AR-C-04 | U1000R2V | 7G1.5 | 55 | X 093 03 | 1 | 4LHA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LHA001AR | 1st floor
|  | 19 | [5 empty] | 8
|  | 20 | [5 empty] | 9 | [6 empty] | #N/A
|  | 21 | [5 empty] | 10
|  | 22 | [5 empty] | 11
| X 251 03 | 40 | [5 empty] | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 05 | 16 | 4KLD001CQ/4LHA001GE-C-01 | U1000R2V | 5G1.5 | 35 | X? | A | 4LHA001GE | 24Vcc |  |  | Flue gas
|  | 37 | [5 empty] | A | [6 empty] | #N/A
|  | 38 | [5 empty] | A
| X 251 03 | 61 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 042 16 | 6 | 4KLD001CQ/4LKA001AR-C-01 | U1000R2V | 7G1.5 | 50 | X 031 09 | 1 | 4LKA001AR | 24Vcc |  |  | Secondary air system
|  | 21 | [5 empty] | 2
|  | 22 | [5 empty] | 3 | [6 empty] | #N/A
|  | 23 | [5 empty] | 4
|  | 24 | [5 empty] | 5
|  | 25 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 042 16 | 7 | 4KLD001CQ/4LKA001AR-C-02 | U1000R2V | 12G1.5 | 55 | X 111 03 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 26 | [5 empty] | 8 | [6 empty] | #N/A
|  | 27 | [5 empty] | 9
|  | 28 | [5 empty] | 10
|  | 29 | [5 empty] | 11 | [6 empty] | #N/A
|  | 30 | [5 empty] | 12
|  | 31 | [5 empty] | 13
|  | 32 | [5 empty] | 14 | [6 empty] | #N/A
|  | 33 | [5 empty] | 15
[7 empty] | X 251 03 | 25
[8 empty] | 26 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 042 16 | 8 | 4KLD001CQ/4LKA001AR-C-03 | U1000R2V | 5G1.5 | 55 | X 113 03 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 34 | [5 empty] | 4 | [6 empty] | #N/A
|  | 35 | [5 empty] | 5
[7 empty] | X 251 03 | 27
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 042 16 | 9 | 4KLD001CQ/4LKA001AR-C-04 | U1000R2V | 12G1.5 | 55 | X 114 03 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 36 | [5 empty] | 9
|  | 37 | [5 empty] | 10 | [6 empty] | #N/A
|  | 38 | [5 empty] | 11
|  | 39 | [5 empty] | 12
|  | 40 | [5 empty] | 13 | [6 empty] | #N/A
|  | 11 |  |  |  |  | X 052 04 | 4
|  | 46 | [5 empty] | 7
| X 043 03 | 3 | [5 empty] | 1 | [6 empty] | #N/A
|  | 32 | [5 empty] | 3
| X 251 03 | 28 |  |  |  |  | X 121 03 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 042 16 | 10 | 4KLD001CQ/4LKA001AR-C-05 | U1000R2V | 7G1.5 | 55 | X 115 03 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 41 | [5 empty] | 9
|  | 42 | [5 empty] | 10 | [6 empty] | #N/A
|  | 43 | [5 empty] | 11
|  | 44 | [5 empty] | 12
|  | 45 | [5 empty] | 13 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 03 | 4 | 4KLD001CQ/4LKA001AR-C-06 | U1000R2V | 5G1.5 | 55 | X 075 04 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 33 | [5 empty] | 2 | [6 empty] | #N/A
|  | 34 | [5 empty] | 3
|  | 35 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD001CQ | X 043 07 | 5 | 4KLD001CQ/4LKA001AR-C-07 | U1000R2V | 5G1.5 | 55 | X 079 04 | 1 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor
|  | 23 | [5 empty] | 5
|  | 24 | [5 empty] | 6 | [6 empty] | #N/A
|  | 25 | [5 empty] | 9
| PE | PE |  |  |  |  | PE | PE
4KLD001CQ | X 043 07 | 26 | 4KLD001CQ/4LKA001AR-C-08 | U1000R2V | 5G1.5 | 55 | X 079 04 | 13 | 4LKA001AR | 24Vcc | SIGNALISATION NUMÉRIQUE DU 4LKA001AR | 1st floor |  |  | WCC 14
|  | 27 | [5 empty] | 14
|  | 28 | [5 empty] | 15
| X 251 03 | 29 | [5 empty] | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | KF 301 | -X1 P2 | 4KLD002CQ/4KLD005CQ-S-01 | Fiber optic |  | 25 | KF 301 03 | -X1 P1 | 4KLD005CQ | 24Vcc |  |  | HP steam
4KLD002CQ | KF 302 | -X1 P2 | 4KLD002CQ/4KLD005CQ-S-02 | Fiber optic |  | 25 | KF 302 03 | -X1 P1 | 4KLD005CQ | 24Vcc |  |  | HP steam |  | #N/A
4KLD002CQ | X 043 12 | 13 | 4KLD002CQ/4LCA002CR-C-01 | U1000R2V | 12G1.5 | 15 | X 030 02 | 1 | 4LCA002CR | 24Vcc |  | 2nd floor | Water steam
|  | 40 | [5 empty] | 4
|  | 41 | [5 empty] | 5 | [6 empty] | #N/A
|  | 42 | [5 empty] | 6
|  | 43 | [5 empty] | 7
|  | 44 | [5 empty] | 8 | [6 empty] | #N/A
|  | 45 | [5 empty] | 9
|  | 46 | [5 empty] | 10
|  | 47 | [5 empty] | 11 | [6 empty] | #N/A
|  | 48 | [5 empty] | 12
| X 251 03 | 218 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 042 14 | 3 | 4KLD002CQ/4LKD001AR-C-01 | U1000R2V | 12G1.5 | 15 | XS 051 03 | 1 | 4LKD001AR | 24Vcc |  |  | Water steam
|  | 13 | [5 empty] | 4
|  | 14 | [5 empty] | 5 | [6 empty] | #N/A
|  | 15 | [5 empty] | 6
|  | 16 | [5 empty] | 7
|  | 17 | [5 empty] | 8 | [6 empty] | #N/A
|  | 18 | [5 empty] | 9
|  | 19 | [5 empty] | 10
|  | 20 | [5 empty] | 11 | [6 empty] | #N/A
|  | 21 | [5 empty] | 12
| X 251 03 | 1 |  |  |  |  | XS 055 03 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 042 14 | 5 | 4KLD002CQ/4LKD002AR-C-01 | U1000R2V | 27G1.5 | 20 | X 087 06 | 1 | 4LKD002AR | 24Vcc |  |  | Ash system
|  | 24 | [5 empty] | 6
|  | 25 | [5 empty] | 7 | [6 empty] | #N/A
|  | 26 | [5 empty] | 9
|  | 27 | [5 empty] | 14
|  | 28 | [5 empty] | 15 | [6 empty] | #N/A
|  | 6 |  |  |  |  | X 092 06 | 1
|  | 29 | [5 empty] | 5
|  | 30 | [5 empty] | 6 | [6 empty] | #N/A
|  | 31 | [5 empty] | 8
|  | 32 | [5 empty] | 13
|  | 7 |  |  |  |  | XS 121 03 | 1 | [6 empty] | #N/A
|  | 33 | [5 empty] | 5
|  | 34 | [5 empty] | 6
|  | 35 | [5 empty] | 7 | [6 empty] | #N/A
|  | 36 | [5 empty] | 8
|  | 37 | [5 empty] | 9
|  | 38 | [5 empty] | 10 | [6 empty] | #N/A
| X 251 03 | 2 |  |  |  |  | XS 125 03 | 1
|  | 3 | [5 empty] | 2
|  | 4 | [5 empty] | 3 | [6 empty] | #N/A
|  | 5 | [5 empty] | 4
|  | 6 | [5 empty] | 5
|  | 7 | [5 empty] | 6 | [6 empty] | #N/A
|  | 8 | [5 empty] | 7
|  | 9 | [5 empty] | 8
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 042 14 | 8 | 4KLD002CQ/4LKD003AR-C-01 | U1000R2V | 27G1.5 | 15 | XS 201 03 | 1 | 4LKD003AR | 24Vcc |  |  | Ash system
|  | 9 |  |  |  |  | X 165 06 | 1
|  | 39 |  |  |  |  | XS 201 03 | 4 | [6 empty] | #N/A
|  | 40 |  |  |  |  | X 165 06 | 13
|  | 41 | [5 empty] | 14
|  | 42 | [5 empty] | 16 | [6 empty] | #N/A
|  | 43 | [5 empty] | 21
|  | 44 | [5 empty] | 22
| X 042 16 | 3 | [5 empty] | 6 | [6 empty] | #N/A
|  | 4 |  |  |  |  | X 172 06 | 1
|  | 13 |  |  |  |  | X 165 06 | 23
|  | 14 | [5 empty] | 24 | [6 empty] | #N/A
|  | 15 | [5 empty] | 25
|  | 16 | [5 empty] | 27
|  | 17 | [5 empty] | 29 | [6 empty] | #N/A
|  | 18 |  |  |  |  | X 172 06 | 6
|  | 19 | [5 empty] | 7
|  | 20 | [5 empty] | 8 | [6 empty] | #N/A
|  | 5 |  |  |  |  | X 177 06 | 1
|  | 21 |  |  |  |  | X 172 06 | 10
|  | 22 | [5 empty] | 11 | [6 empty] | #N/A
|  | 23 | [5 empty] | 12
|  | 24 |  |  |  |  | X 177 06 | 6
|  | 25 | [5 empty] | 7 | [6 empty] | #N/A
|  | 26 | [5 empty] | 8
|  | 27 | [5 empty] | 10
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 042 16 | 28 | 4KLD002CQ/4LKD003AR-C-02 | U1000R2V | 12G1.5 | 15 | X 182 06 | 1 | 4LKD003AR | 24Vcc |  | 2nd floor
|  | 6 | [5 empty] | 9
|  | 29 | [5 empty] | 6 | [6 empty] | #N/A
|  | 30 | [5 empty] | 7
|  | 31 | [5 empty] | 14
|  | 32 | [5 empty] | 15 | [6 empty] | #N/A
|  | 33 |  |  |  |  | X 177 06 | 11
|  | 34 | [5 empty] | 12
| X 251 03 | 13 |  |  |  |  | XS 205 03 | 1 | [6 empty] | #N/A
|  | 14 | [5 empty] | 2
|  | 15 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 12 | 11 | 4KLD002CQ/4LKD003AR-C-03 | U1000R2V | 12G1.5 | 15 | X 187 06 | 1 | 4LKD003AR | 24Vcc |  | 2nd floor
|  | 34 | [5 empty] | 6
|  | 35 | [5 empty] | 7 | [6 empty] | #N/A
|  | 36 | [5 empty] | 9
|  | 37 | [5 empty] | 14
|  | 38 | [5 empty] | 15 | [6 empty] | #N/A
| X 251 03 | 20 |  |  |  |  | XS 205 03 | 9
|  | 21 | [5 empty] | 10
|  | 22 | [5 empty] | 11 | [6 empty] | #N/A
|  | 23 | [5 empty] | 12
|  | 24 | [5 empty] | 13
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 042 16 | 7 | 4KLD002CQ/4LKD004AR-C-01 | U1000R2V | 27G1.5 | 15 | XS 291 03 | 1 | 4LKD004AR | 24Vcc |  |  | Ash system
|  | 8 |  |  |  |  | X 255 06 | 1
|  | 35 |  |  |  |  | XS 291 03 | 4 | [6 empty] | #N/A
|  | 36 |  |  |  |  | X 255 06 | 6
|  | 9 |  |  |  |  | X 260 06 | 1
|  | 37 |  |  |  |  | X 255 06 | 7 | [6 empty] | #N/A
|  | 38 | [5 empty] | 9
|  | 39 | [5 empty] | 14
|  | 40 | [5 empty] | 15 | [6 empty] | #N/A
|  | 41 |  |  |  |  | X 260 06 | 5
|  | 42 | [5 empty] | 6
|  | 43 | [5 empty] | 8 | [6 empty] | #N/A
|  | 44 | [5 empty] | 13
| X 043 03 | 3 |  |  |  |  | X 265 06 | 1
|  | 4 |  |  |  |  | X 270 06 | 1 | [6 empty] | #N/A
|  | 15 |  |  |  |  | X 265 06 | 5
|  | 16 | [5 empty] | 6
|  | 17 | [5 empty] | 8 | [6 empty] | #N/A
|  | 18 | [5 empty] | 13
|  | 19 |  |  |  |  | X 270 06 | 6
|  | 20 | [5 empty] | 7 | [6 empty] | #N/A
|  | 21 | [5 empty] | 9
|  | 22 | [5 empty] | 14
|  | 23 | [5 empty] | 15 | [6 empty] | #N/A
| X 251 03 | 25 |  |  |  |  | XS 295 02 | 1
|  | 26 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 03 | 5 | 4KLD002CQ/4LKD005AR-C-01 | U1000R2V | 12G1.5 | 15 | XS 381 03 | 1 | 4LKD005AR | 24Vcc |  |  | Ash system
|  | 6 |  |  |  |  | X 345 06 | 1
|  | 24 |  |  |  |  | XS 381 03 | 4 | [6 empty] | #N/A
|  | 25 |  |  |  |  | X 345 06 | 6
|  | 26 | [5 empty] | 7
|  | 27 | [5 empty] | 8 | [6 empty] | #N/A
|  | 28 | [5 empty] | 10
|  | 29 | [5 empty] | 11
|  | 30 | [5 empty] | 12 | [6 empty] | #N/A
|  | 7 |  |  |  |  | X 350 06 | 1
|  | 31 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 03 | 32 | 4KLD002CQ/4LKD005AR-C-02 | U1000R2V | 27G1.5 | 15 | X 350 06 | 1 | 4LKD005AR | 24Vcc |  | 2nd floor
|  | 33 | [5 empty] | 7
|  | 34 | [5 empty] | 8 | [6 empty] | #N/A
|  | 35 | [5 empty] | 10
|  | 36 | [5 empty] | 11
|  | 8 | [5 empty] | 12 | [6 empty] | #N/A
|  | 37 |  |  |  |  | X 355 06 | 5
|  | 38 | [5 empty] | 6
|  | 9 | [5 empty] | 8 | [6 empty] | #N/A
|  | 39 | [5 empty] | 13
|  | 40 |  |  |  |  | X 360 06 | 5
|  | 41 | [5 empty] | 6 | [6 empty] | #N/A
|  | 42 | [5 empty] | 8
|  | 43 | [5 empty] | 13
|  | 44 | [5 empty] | 1 | [6 empty] | #N/A
|  | 27 |  |  |  |  | XS 385 02 | 1
|  | 28 | [5 empty] | 2
| X 251 03 | 29 | [5 empty] | 3 | [6 empty] | #N/A
|  | 30 | [5 empty] | 4
|  | 31 | [5 empty] | 5
|  | 32 | [5 empty] | 6 | [6 empty] | #N/A
|  | 33 | [5 empty] | 7
|  | 34 | [5 empty] | 8
|  | 35 | [5 empty] | 9 | [6 empty] | #N/A
|  | 36 | [5 empty] | 10
|  | 37 | [5 empty] | 11
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 03 | 10 | 4KLD002CQ/4LKD006AR-C-01 | U1000R2V | 12G1.5 | 20 | XS 461 03 | 1 | 4LKD006AR | 24Vcc |  |  | Ash system
|  | 11 |  |  |  |  | X 425 06 | 1
|  | 45 |  |  |  |  | XS 461 03 | 4 | [6 empty] | #N/A
|  | 46 |  |  |  |  | X 425 06 | 3
| X 043 05 | 3 | [5 empty] | 4
|  | 13 | [5 empty] | 9 | [6 empty] | #N/A
|  | 14 | [5 empty] | 10
|  | 15 | [5 empty] | 12
|  | 16 | [5 empty] | 13 | [6 empty] | #N/A
|  | 17 | [5 empty] | 14
| X 251 03 | 40 |  |  |  |  | XS 465 03 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 05 | 4 | 4KLD002CQ/4LKD006AR-C-02 | U1000R2V | 27G1.5 | 20 | X 430 06 | 6 | 4LKD006AR | 24Vcc |  | 2nd floor
|  | 18 | [5 empty] | 7
|  | 19 | [5 empty] | 8 | [6 empty] | #N/A
|  | 20 | [5 empty] | 1
|  | 5 | [5 empty] | 1
|  | 6 | [5 empty] | 10 | [6 empty] | #N/A
|  | 21 | [5 empty] | 11
|  | 22 | [5 empty] | 12
|  | 23 |  |  |  |  | X 435 06 | 1 | [6 empty] | #N/A
|  | 24 | [5 empty] | 5
|  | 25 | [5 empty] | 6
|  | 26 | [5 empty] | 8 | [6 empty] | #N/A
|  | 27 | [5 empty] | 13
|  | 28 |  |  |  |  | X 440 06 | 5
|  | 29 | [5 empty] | 6 | [6 empty] | #N/A
|  | 30 | [5 empty] | 8
|  | 31 | [5 empty] | 13
| X 251 03 | 41 | [5 empty] | 2 | [6 empty] | #N/A
|  | 42 | [5 empty] | 3
|  | 43 | [5 empty] | 4
|  | 44 | [5 empty] | 5 | [6 empty] | #N/A
|  | 45 | [5 empty] | 6
|  | 46 | [5 empty] | 7
|  | 47 | [5 empty] | 8 | [6 empty] | #N/A
|  | 48 | [5 empty] | 9
|  | 49 | [5 empty] | 10
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 05 | 7 | 4KLD002CQ/4LKD007AR-C-01 | U1000R2V | 12G1.5 | 12 | X 523 06 | 1 | 4LKD007AR | 24Vcc |  |  | Drain&Vent
|  | 32 | [5 empty] | 5
|  | 8 |  |  |  |  | X 526 06 | 1 | [6 empty] | #N/A
|  | 33 |  |  |  |  | X 523 06 | 7
|  | 34 |  |  |  |  | X 526 06 | 5
|  | 35 | [5 empty] | 7 | [6 empty] | #N/A
| X 043 12 | 14 |  |  |  |  | XS 534 03 | 1
|  | 49 | [5 empty] | 4
| X 251 03 | 52 |  |  |  |  | XS 551 02 | 1 | [6 empty] | #N/A
|  | 53 | [5 empty] | 2
|  | 54 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 12 | 14 | 4KLD002CQ/4LKD007AR-C-02 | U1000R2V | 12G1.5 | 20 |  |  | 4LKD007AR | 24Vcc |  | 2nd floor
49
|  | 9 | [5 empty] | 1 | [6 empty] | #N/A
|  | 10 | [5 empty] | 3
|  | 30 | [5 empty] | 6
|  | 31 | [5 empty] | 7 | [6 empty] | #N/A
|  | 32 | [5 empty] | 8
|  | 33 | [5 empty] | 9
|  | 84 | [5 empty] | 1 | [6 empty] | #N/A
|  | 85 | [5 empty] | 2
|  | 86 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 05 | 9 | 4KLD002CQ/4LKF001AR-C-01 | U1000R2V | 12G1.5 | 35 | XS 051 03 | 1 | 4LKF001AR | 24Vcc |  |  | Condensate system
|  | 36 | [5 empty] | 4
|  | 37 | [5 empty] | 5 | [6 empty] | #N/A
|  | 38 | [5 empty] | 6
|  | 39 | [5 empty] | 7
|  | 40 | [5 empty] | 8 | [6 empty] | #N/A
|  | 41 | [5 empty] | 9
|  | 42 | [5 empty] | 10
|  | 43 | [5 empty] | 11 | [6 empty] | #N/A
|  | 44 | [5 empty] | 12
| X 251 03 | 59 |  |  |  |  | XS 055 03 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 07 | 3 | 4KLD002CQ/4LKF002AR-C-01 | U1000R2V | 12G1.5 | 15 | X 084 06 | 1 | 4LKF002AR | 24Vcc |  |  | Water steam
|  | 4 |  |  |  |  | X 087 06 | 1
|  | 5 |  |  |  |  | X 090 06 | 1 | [6 empty] | #N/A
|  | 6 |  |  |  |  | XS 111 03 | 1
|  | 19 |  |  |  |  | X 084 06 | 5
|  | 20 | [5 empty] | 7 | [6 empty] | #N/A
|  | 21 |  |  |  |  | X 087 06 | 5
|  | 22 | [5 empty] | 7
|  | 23 |  |  |  |  | X 090 06 | 5 | [6 empty] | #N/A
|  | 24 | [5 empty] | 7
|  | 25 |  |  |  |  | XS 111 03 | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 07 | 27 | 4KLD002CQ/4LKF002AR-C-02 | U1000R2V | 7G1.5 | 15 | XS 111 03 | 7 | 4LKF002AR | 24Vcc |  | 2nd floor | Water steam
|  | 28 | [5 empty] | 8
|  | 29 | [5 empty] | 9 | [6 empty] | #N/A
| X 043 12 | 12 | [5 empty] | 1
|  | 39 | [5 empty] | 7
|  | 26 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 043 07 | 7 | 4KLD002CQ/4LKF003AR-C-01 | U1000R2V | 27G1.5 | 20 | XS 181 03 | 1 | 4LKF003AR | 24Vcc |  |  | Fluegas recirculation system
|  | 8 |  |  |  |  | X 154 06 | 1 | [6 empty] | #N/A
|  | 30 |  |  |  |  | XS 181 03 | 4
|  | 31 |  |  |  |  | X 154 06 | 5
|  | 32 | [5 empty] | 7 | [6 empty] | #N/A
|  | 10 |  |  |  |  | X 161 06 | 1
|  | 11 |  |  |  |  | X 165 06 | 1
|  | 12 |  |  |  |  | X 168 06 | 1 | [6 empty] | #N/A
|  | 35 |  |  |  |  | X 161 06 | 7
|  | 36 | [5 empty] | 8
|  | 37 | [5 empty] | 10 | [6 empty] | #N/A
|  | 38 | [5 empty] | 15
|  | 39 | [5 empty] | 16
|  | 40 |  |  |  |  | X 165 06 | 5 | [6 empty] | #N/A
|  | 41 | [5 empty] | 7
|  | 42 |  |  |  |  | X 168 06 | 5
|  | 43 | [5 empty] | 7 | [6 empty] | #N/A
| X 251 03 | 60 |  |  |  |  | XS 185 03 | 1
|  | 61 | [5 empty] | 2
|  | 62 | [5 empty] | 3 | [6 empty] | #N/A
|  | 63 | [5 empty] | 4
|  | 64 | [5 empty] | 5
|  | 65 | [5 empty] | 6 | [6 empty] | #N/A
|  | 66 | [5 empty] | 7
|  | 67 | [5 empty] | 5
|  | 68 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 043 07 | 13 | 4KLD002CQ/4LKF004AR-C-01 | U1000R2V | 12G1.5 | 15 | XS 251 03 | 1 | 4LKF004AR | 24Vcc |  |  | Ash removal system
|  | 14 |  |  |  |  | X 228 06 | 1 | [6 empty] | #N/A
|  | 15 |  |  |  |  | X 232 06 | 1
|  | 44 |  |  |  |  | XS 251 03 | 4
|  | 45 |  |  |  |  | X 228 06 | 7 | [6 empty] | #N/A
|  | 46 | [5 empty] | 8
|  | 47 | [5 empty] | 10
|  | 48 | [5 empty] | 15 | [6 empty] | #N/A
|  | 49 | [5 empty] | 16
|  | 50 |  |  |  |  | X 232 06 | 3
| X 251 03 | 71 |  |  |  |  | XS 255 03 | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 043 09 | 3 | 4KLD002CQ/4LKF004AR-C-02 | U1000R2V | 12G1.5 | 15 | X 235 06 | 4 | 4LKF004AR | 24Vcc |  | 2nd floor
|  | 4 | [5 empty] | 1 | [6 empty] | #N/A
|  | 12 | [5 empty] | 8
|  | 13 | [5 empty] | 5
|  | 14 | [5 empty] | 7 | [6 empty] | #N/A
| X 251 03 | 72 |  |  |  |  | XS 255 03 | 3
|  | 73 | [5 empty] | 4
|  | 74 | [5 empty] | 5 | [6 empty] | #N/A
|  | 75 | [5 empty] | 6
|  | 76 | [5 empty] | 4
|  | 77 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | 6
4KLD002CQ | X 043 09 | 5 | 4KLD002CQ/4LKF005AR-C-01 | U1000R2V | 7G1.5 | 15 | X 371 04 | 1 | 4LKF005AR | 24Vcc |  |  | Condensate system
|  | 6 | [5 empty] | 3 | [6 empty] | #N/A
|  | 15 | [5 empty] | 6
|  | 16 | [5 empty] | 7
|  | 17 | [5 empty] | 8 | [6 empty] | #N/A
|  | 18 | [5 empty] | 9
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 043 12 | 7 | 4KLD002CQ/4LKF005AR-C-02 | U1000R2V | 7G1.5 | 15 | X 375 04 | 1 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system |  | WCC 14
|  | 8 | [5 empty] | 3
|  | 26 | [5 empty] | 6
|  | 27 | [5 empty] | 7 | [6 empty] | #N/A
|  | 28 | [5 empty] | 8
|  | 29 | [5 empty] | 9
| PE | PE |  |  |  |  | PE | 3 | [6 empty] | #N/A
4KLD002CQ | X 043 16 | 11 | 4KLD002CQ/4LKF005AR-M-01 | 12IP09EISF BU | 12x2x0.88 | 15 | X 323 05 | 9 | 4LKF005AR | 24Vcc |  |  | Condensate system
|  | 12 | [5 empty] | 10
|  | 13 | [5 empty] | 11 | [6 empty] | #N/A
|  | 15 | [5 empty] | 13
|  | 16 | [5 empty] | 14
|  | 17 | [5 empty] | 15 | [6 empty] | #N/A
|  | 3 | [5 empty] | 17
|  | 19 | [5 empty] | 18
|  | 4 | [5 empty] | 19 | [6 empty] | #N/A
|  | 20 | [5 empty] | 20
|  | 5 | [5 empty] | A
|  | 21 | [5 empty] | A | [6 empty] | #N/A
|  | 6 | [5 empty] | A
|  | 22 | [5 empty] | A
|  | 23 |  |  |  |  | X 337 08 | 1 | [6 empty] | #N/A
|  | 24 | [5 empty] | 2
|  | 7 |  |  |  |  | X 327 05 | 17
|  | 25 | [5 empty] | 18 | [6 empty] | #N/A
| X 044 03 | 2 | [5 empty] | 19
|  | 8 | [5 empty] | 20
|  | 9 | [5 empty] | 9 | [6 empty] | #N/A
|  | 10 | [5 empty] | 10
|  | 11 | [5 empty] | 11
| X 251 03 | 90 |  |  |  |  | X 391 03 | 21 | [6 empty] | #N/A
4KLD002CQ | X 044 03 | 13 | 4KLD002CQ/4LKF005AR-M-02 | 08IP09EISF | 8x2x0.88 | 15 | X 327 05 | 13 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system
|  | 14 | [5 empty] | 14
|  | 15 | [5 empty] | 15 | [6 empty] | #N/A
|  | 17 |  |  |  |  | X 337 08 | 3
|  | 18 | [5 empty] | 4
| X 135 03 | 1 |  |  |  |  | X 323 05 | 1 | [6 empty] | #N/A
|  | 2 | [5 empty] | 2
|  | 3 |  |  |  |  | X 327 05 | 1
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 91 | [5 empty] | 22
|  | 92 |  |  |  |  | X 391 03 | 23
|  | 93 | [5 empty] | 24 | [6 empty] | #N/A
|  | 94 | [5 empty] | 25
|  | 95 | [5 empty] | 26
|  | 96 | [5 empty] | 27 | [6 empty] | #N/A
|  | 97 | [5 empty] | 28
4KLD002CQ | X 044 03 | 23 | 4KLD002CQ/4LKF005AR-M-03 | 12IP09EISF | 12x2x0.88 | 15 | X 331 05 | 9 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system
|  | 24 | [5 empty] | 10 | [6 empty] | #N/A
|  | 25 | [5 empty] | 11
|  | 27 | [5 empty] | 13
|  | 28 | [5 empty] | 14 | [6 empty] | #N/A
|  | 29 | [5 empty] | 15
| X 044 05 | 2 | [5 empty] | 17
|  | 11 | [5 empty] | 18 | [6 empty] | #N/A
|  | 3 | [5 empty] | 19
|  | 12 | [5 empty] | 20
|  | 4 | [5 empty] | A | [6 empty] | #N/A
|  | 13 | [5 empty] | A
|  | 5 | [5 empty] | A
|  | 14 | [5 empty] | A | [6 empty] | #N/A
|  | 15 |  |  |  |  | X 338 05 | 1
|  | 16 | [5 empty] | 2
|  | 17 |  |  |  |  | X 335 05 | 9 | [6 empty] | #N/A
|  | 18 | [5 empty] | 10
|  | 19 | [5 empty] | 11
|  | 21 | [5 empty] | 13 | [6 empty] | #N/A
|  | 22 | [5 empty] | 14
|  | 23 | [5 empty] | 15
|  | 7 | [5 empty] | 17 | [6 empty] | #N/A
|  | 25 | [5 empty] | 18
4KLD002CQ | X 044 07 | 2 | 4KLD002CQ/4LKF005AR-M-04 | 08IP09EISF | 8x2x0.88 | 15 | X 335 05 | 19 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system
|  | 8 | [5 empty] | 20 | [6 empty] | #N/A
|  | 9 | [5 empty] | 3
|  | 10 | [5 empty] | 4
|  | 1 | [5 empty] | 1 | [6 empty] | #N/A
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 1
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
|  | 156 | [5 empty] | 29
|  | 157 | [5 empty] | 30
|  | 158 | [5 empty] | 31 | [6 empty] | #N/A
|  | 159 | [5 empty] | 32
|  | 160 | [5 empty] | 33
|  | 161 | [5 empty] | 34 | [6 empty] | #N/A
|  | 162 | [5 empty] | 35
|  | 163 | [5 empty] | 36
4KLD002CQ | X 042 14 | 4 | 4KLD002CQ/4LKF006AR-C-01 | U1000R2V | 7G1.5 | 15 | X 591 04 | 1 | 4LKF006AR | 24Vcc |  |  | Drain&Vent |  | WCC 14
|  | 22 | [5 empty] | 6
|  | 23 | [5 empty] | 7
| X 043 07 | 33 | [5 empty] | 8 | [6 empty] | #N/A
|  | 34 | [5 empty] | 9
| X 251 03 | 106 |  |  |  |  | X 391 03 | 13
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 12 | 6 | 4KLD002CQ/4LKF006AR-C-02 | U1000R2V | 7G1.5 | 22 |  |  | 4LKF006AR | 24Vcc |  | 2nd floor
24
|  | 25 | [12 empty] | #N/A
|  | 169 | [5 empty] | 18
|  | 170 | [5 empty] | 19
|  | 171 | [5 empty] | 20 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 044 03 | 19 | 4KLD002CQ/4LKF006AR-M-01 | 04IP09EISF BU | 4x2x0.88 | 15 | X? | ?? | 4LKF006AR | 24Vcc |  |  | Drain&Vent
|  | 20 | [5 empty] | ?? | [6 empty] | #N/A
|  | 21 | [5 empty] | ??
|  | 22 | [5 empty] | ??
| X 135 03 | 5 |  |  |  |  | X 543 05 | 1 | [6 empty] | #N/A
|  | 6 | [5 empty] | 2
|  | 7 |  |  |  |  | X 546 09 | 1
|  | 8 | [5 empty] | 2 | [6 empty] | #N/A
4KLD002CQ | X 044 07 | 11 | 4KLD002CQ/4LKF006AR-M-02 | 04IP09EISF | 4x2x0.88 | 22 | X 554 08 | 1 | 4LKF006AR | 24Vcc |  | 2nd floor
|  | 12 | [5 empty] | 2
|  | 5 | [12 empty] | #N/A
6
|  | 172 | [5 empty] | 21
|  | 173 | [5 empty] | 22 | [6 empty] | #N/A
|  | 174 | [5 empty] | 23
|  | 175 | [5 empty] | 24
4KLD002CQ | X 043 09 | 7 | 4KLD002CQ/4LKM001AR-C-01 | U1000R2V | 27G1.5 | 10 | X 040 04 | 1 | 4LKM001AR | 24Vcc |  |  | Drain&Vent |  | #DIV/0!
|  | 19 | [5 empty] | 8
|  | 20 | [5 empty] | 9
|  | 21 | [5 empty] | 10 | [6 empty] | #N/A
|  | 22 | [5 empty] | 11
|  | 23 | [5 empty] | 12
|  | 24 | [5 empty] | 13 | [6 empty] | #N/A
|  | 25 | [5 empty] | 14
|  | 26 | [5 empty] | 15
|  | 27 | [5 empty] | 16 | [6 empty] | #N/A
|  | 28 | [5 empty] | 17
|  | 29 | [5 empty] | 18
|  | 30 | [5 empty] | 19 | [6 empty] | #N/A
|  | 31 | [5 empty] | 20
|  | 32 | [5 empty] | 21
|  | 33 | [5 empty] | 22 | [6 empty] | #N/A
|  | 34 | [5 empty] | 23
|  | 35 | [5 empty] | 24
|  | 36 | [5 empty] | 25 | [6 empty] | #N/A
|  | 37 | [5 empty] | 26
|  | 38 | [5 empty] | 27
|  | 39 | [5 empty] | 28 | [6 empty] | #N/A
|  | 40 | [5 empty] | 29
|  | 41 | [5 empty] | 30
| X 251 03 | 126 |  |  |  |  | X? | A | [6 empty] | #N/A
|  | 127 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLD002CQ | X 043 12 | 4 | 4KLD002CQ/4LKM001CR-C-01 | U1000R2V | 7G1.5 | 10 | X 060 04 | 1 | 4LKM001CR | 24Vcc |  |  |  |  | WCC 14
|  | 20 | [5 empty] | 4
|  | 21 | [5 empty] | 5
#N/A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 044 12 | 5 | 4KLD002CQ/4LKM001CR-C-02 | U1000R2V | 12G1.5 | 15 | X 050 03 | 1 | 4LKM001CR | 24Vcc |  | 2nd floor
|  | 4 | [5 empty] | 7
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4
|  | 9 | [5 empty] | 5 | [6 empty] | #N/A
|  | 10 | [5 empty] | 6
| X 251 03 | 135 |  |  |  |  | X? | A
|  | 136 | [5 empty] | A | [6 empty] | #N/A
|  | 137 | [5 empty] | A
|  | 138 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD002CQ | X 043 12 | 5 | 4KLD002CQ/4LKM002CR-C-01 | U1000R2V | 7G1.5 | 10 | X 050 04 | 1 | 4LKM002CR | 400Vca
|  | 22 | [5 empty] | 4
|  | 23 | [5 empty] | 6 | [6 empty] | #N/A
| X 251 03 | 139 |  |  |  |  | X? | A
|  | 140 | [5 empty] | A
|  | 141 | [5 empty] | A | [6 empty] | #N/A
A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 043 05 | 3 | 4KLD003CQ/4CRF152BJ-C-01 | U1000R2V | 7G1.5 | 12 | X? | ?? | 4CRF152BJ | 24Vcc |  |  | Cooling water system |  | WCC 14
|  | 13 | [5 empty] | ??
|  | 21 | [5 empty] | ??
| X 045 12 | 21 |  |  |  |  | X 032 03 | 2 | [6 empty] | #N/A
|  | 9 | [5 empty] | 1
| X 251 03 | 101 |  |  |  |  | X 033 03 | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 043 05 | 4 | 4KLD003CQ/4FDR005BJ-C-01 | U1000R2V | 7G1.5 | 60 | X? | ?? | 4FDR005BJ | 24Vcc |  |  | Ash system
|  | 14 | [5 empty] | ??
|  | 22 | [5 empty] | ?? | [6 empty] | #N/A
|  | 23 | [5 empty] | ??
| X 045 12 | 22 |  |  |  |  | X 032 03 | 2
|  | 10 | [5 empty] | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | KF 301 03 | -X1 P2 | 4KLD003CQ/4KLD004CQ-S-01 |  |  | 25 | KF 301 03 | -X1 P1 | 4KLD004CQ | 24Vcc |  |  | Water steam
4KLD003CQ | KF 302 03 | -X1 P2 | 4KLD003CQ/4KLD004CQ-S-02 |  |  | 25 | KF 302 03 | -X1 P1 | 4KLD004CQ | 24Vcc |  |  | Water steam |  | #N/A
4KLD003CQ | X 043 03 | 4 | 4KLD003CQ/4LCA001BJ-C-01 | U1000R2V | 7G1.5 | 52 | X 031 03 | 1 | 4LCA001BJ | 24Vcc |  |  | Ash removal system
|  | 14 | [5 empty] | 14
|  | 31 | [5 empty] | 21 | [6 empty] | #N/A
|  | 32 | [5 empty] | 22
|  | 33 | [5 empty] | 23
|  | 34 | [5 empty] | 24 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 043 05 | 26 | 4KLD003CQ/4LCA001BJ-C-02 | U1000R2V | 12G1.5 | 52 | X 031 03 | 27 | 4LCA001BJ | 24Vcc |  | 3rd floor to outside
|  | 27 | [5 empty] | 28 | [6 empty] | #N/A
|  | 28 | [5 empty] | 29
|  | 29 | [5 empty] | 30
|  | 30 | [5 empty] | 31 | [6 empty] | #N/A
|  | 123 | [5 empty] | 1
|  | 124 | [5 empty] | 2
|  | 125 | [5 empty] | 3 | [6 empty] | #N/A
|  | 126 | [5 empty] | 4
|  | 127 | [5 empty] | 5
|  | 128 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 214 10 | 3 | 4KLD003CQ/4LCA001BJ-C-03 | U1000R2V | 5G1.5 | 52 | X 041 03 | 1 | 4LCA001BJ | 230Vac |  | 3rd floor to outside
|  | 7 | [5 empty] | 5 | [6 empty] | #N/A
|  | 8 | [5 empty] | 6
|  | 6 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 043 07 | 2 | 4KLD003CQ/4LCA001BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 52 | X 051 03 | 1 | 4LCA001BJ | 24Vcc |  |  | Ash removal system
|  | 7 | [5 empty] | 9
|  | 8 | [5 empty] | 10 | [6 empty] | #N/A
|  | 9 | [5 empty] | 11
|  | 10 | [5 empty] | 12
|  | 11 | [5 empty] | 5 | [6 empty] | #N/A
|  | 12 | [5 empty] | 13
|  | 13 | [5 empty] | 6
|  | 14 | [5 empty] | 14 | [6 empty] | #N/A
|  | 15 | [5 empty] | 7
|  | 16 | [5 empty] | 15
|  | 17 | [5 empty] | 8 | [6 empty] | #N/A
|  | 18 | [5 empty] | 16
| X 043 09 | 9 | [5 empty] | 17
|  | 10 | [5 empty] | 21 | [6 empty] | #N/A
| X 251 03 | 4 |  |  |  |  | X 071 03 | 3
4KLD003CQ | X 043 09 | 2 | 4KLD003CQ/4LCA001BJ-M-02 | 08IP09EISF | 8x2x0.88 | 52 | X 051 03 | 18 | 4LCA001BJ | 24Vcc |  | 3rd floor to outside
|  | 11 | [5 empty] | 22 | [6 empty] | #N/A
|  | 12 | [5 empty] | 23
|  | 13 | [5 empty] | 24
|  | 3 | [5 empty] | 25 | [6 empty] | #N/A
|  | 10 | [5 empty] | 30
|  | 11 | [5 empty] | 31
|  | 12 | [5 empty] | 32 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
|  | 11 | [5 empty] | 11
|  | 12 | [5 empty] | 12
|  | 13 | [5 empty] | 13 | [6 empty] | #N/A
|  | 14 | [5 empty] | 14
|  | 15 | [5 empty] | 15
4KLD003CQ | X 043 03 | 5 | 4KLD003CQ/4LCA002BJ-C-01 | U1000R2V | 12G1.5 | 90 | X 031 03 | 1 | 4LCA002BJ | 24Vcc |  |  | Thermal water treatment |  | #N/A
|  | 15 | [5 empty] | 6
|  | 39 | [5 empty] | 11
|  | 40 | [5 empty] | 12 | [6 empty] | #N/A
|  | 41 | [5 empty] | 13
|  | 42 | [5 empty] | 14
| X 043 05 | 5 | [5 empty] | 16 | [6 empty] | #N/A
|  | 15 | [5 empty] | 26
|  | 24 | [5 empty] | 36
|  | 25 | [5 empty] | 37 | [6 empty] | #N/A
|  | 26 | [5 empty] | 38
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 043 05 | 27 | 4KLD003CQ/4LCA002BJ-C-02 | U1000R2V | 12G1.5 | 90 | X 031 03 | 39 | 4LCA002BJ | 24Vcc |  | 3rd floor to outside |  |  | #N/A
|  | 28 | [5 empty] | 40
|  | 29 | [5 empty] | 41
|  | 30 | [5 empty] | 42 | [6 empty] | #N/A
|  | 31 | [5 empty] | 43
|  | 16 | [5 empty] | 1
|  | 17 | [5 empty] | 2 | [6 empty] | #N/A
|  | 18 | [5 empty] | 3
|  | 19 | [5 empty] | 4
|  | 20 | [5 empty] | 5 | [6 empty] | #N/A
|  | 21 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 043 09 | 3 | 4KLD003CQ/4LCA002BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 90 | X 051 03 | 1 | 4LCA002BJ | 24Vcc |  |  | Thermal water treatment |  | #N/A
|  | 14 | [5 empty] | 5
|  | 15 | [5 empty] | 6
|  | 16 | [5 empty] | 7 | [6 empty] | #N/A
|  | 17 | [5 empty] | 8
| X 043 12 | 2 | [5 empty] | 9
|  | 9 | [5 empty] | 16 | [6 empty] | #N/A
|  | 10 | [5 empty] | 17
|  | 11 | [5 empty] | 18
|  | 12 | [5 empty] | 19 | [6 empty] | #N/A
|  | 13 | [5 empty] | 20
|  | 14 | [5 empty] | 21
|  | 15 | [5 empty] | 22 | [6 empty] | #N/A
| X 045 05 | 5 | [5 empty] | 23
|  | 14 | [5 empty] | 24
| X 128 03 | 1 |  |  |  |  | X 061 03 | 1 | [6 empty] | #N/A
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
|  | 4 | [5 empty] | 4 | [6 empty] | #N/A
| X 044 05 | 3 |  |  |  |  | X 051 03 | 25
|  | 12 | [5 empty] | 26
| X 251 03 | 14 |  |  |  |  | X 071 03 | 2 | [6 empty] | #N/A
|  | 15 | [5 empty] | 3
|  | 16 | [5 empty] | 4
4KLD003CQ | X 043 03 | 6 | 4KLD003CQ/4LCA102BJ-C-01 | U1000R2V | 7G1.5 | 75 | X 031 03 | 1 | 4LCA102BJ | 24Vcc |  |  | Pneumatic rapping system |  | WCC 14
|  | 16 | [5 empty] | 4
|  | 43 | [5 empty] | 7
|  | 44 | [5 empty] | 8 | [6 empty] | #N/A
| X 251 03 | 17 |  |  |  |  | X 071 03 | 1
|  | 18 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 043 12 | 5 | 4KLD003CQ/4LCA102BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 75 | X 051 03 | 1 | 4LCA102BJ | 24Vcc |  |  | Pneumatic rapping system
|  | 16 | [5 empty] | 2
| X 043 14 | 2 | [5 empty] | 3 | [6 empty] | #N/A
|  | 7 | [5 empty] | 11
|  | 8 | [5 empty] | 12
|  | 9 | [5 empty] | 13 | [6 empty] | #N/A
|  | 10 | [5 empty] | 14
|  | 11 | [5 empty] | 15
|  | 12 | [5 empty] | 16 | [6 empty] | #N/A
|  | 13 | [5 empty] | 17
|  | 14 | [5 empty] | 18
| X 043 16 | 2 | [5 empty] | 22 | [6 empty] | #N/A
|  | 9 | [5 empty] | 20
|  | 10 | [5 empty] | 23
|  | 11 | [5 empty] | 24 | [6 empty] | #N/A
| X 251 03 | 19 |  |  |  |  | X 071 03 | 3
4KLD003CQ | X 128 03 | 5 | 4KLD003CQ/4LCA102BJ-M-02 | 08IP09EISF | 8x2x0.88 | 75 | X 051 03 | 1 | 4LCA102BJ | 24Vcc |  | 3rd floor to outside
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4
|  | 1 | [5 empty] | 5 | [6 empty] | #N/A
|  | 2 | [5 empty] | 6
|  | 3 | [5 empty] | 7
|  | 4 | [5 empty] | 8 | [6 empty] | #N/A
|  | 28 | [5 empty] | 6
|  | 29 | [5 empty] | 7
|  | 30 | [5 empty] | 8 | [6 empty] | #N/A
|  | 31 | [5 empty] | 9
|  | 32 | [5 empty] | 10
|  | 33 | [5 empty] | 11 | [6 empty] | #N/A
|  | 34 | [5 empty] | 12
|  | 35 | [5 empty] | 13
4KLD003CQ | X 045 16 | 2 | 4KLD003CQ/4LCA204BJ-C-01 | U1000R2V | 3G1.5 | 70 | X 051 02 | 1 | 4LCA204BJ | 24Vcc |  |  | Primary air system |  | WCC 14
|  | 6 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 043 16 | 4 | 4KLD003CQ/4LCA204BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 70 | X 051 04 | 1 | 4LCA204BJ | 24Vcc |  |  | Primary air system |  | #N/A
|  | 12 | [5 empty] | 6
|  | 13 | [5 empty] | 7
|  | 14 | [5 empty] | 8 | [6 empty] | #N/A
|  | 15 | [5 empty] | 9
|  | 16 | [5 empty] | 10
| X 044 03 | 2 | [5 empty] | 11 | [6 empty] | #N/A
|  | 9 | [5 empty] | 16
|  | 10 | [5 empty] | 17
|  | 11 | [5 empty] | 18 | [6 empty] | #N/A
|  | 12 | [5 empty] | 19
|  | 13 | [5 empty] | 20
| X 045 05 | 4 | [5 empty] | 21 | [6 empty] | #N/A
|  | 13 | [5 empty] | 22
| X 129 03 | 5 |  |  |  |  | X 061 03 | 1
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
4KLD003CQ | X 129 03 | 7 | 4KLD003CQ/4LCA204BJ-M-02 | 08IP09EISF | 8x2x0.88 | 70 | X 061 03 | 3 | 4LCA204BJ | 24Vcc |  | 3rd floor to outside
|  | 8 | [5 empty] | 4
|  | 1 | [5 empty] | 5 | [6 empty] | #N/A
|  | 2 | [5 empty] | 6
|  | 3 | [5 empty] | 7
|  | 4 | [5 empty] | 8 | [6 empty] | #N/A
|  | 5 | [5 empty] | 9
|  | 6 | [5 empty] | 10
|  | 36 | [5 empty] | 1 | [6 empty] | #N/A
|  | 37 | [5 empty] | 2
|  | 38 | [5 empty] | 3
|  | 39 | [5 empty] | 4 | [6 empty] | #N/A
|  | 40 | [5 empty] | 5
|  | 41 | [5 empty] | 6
|  | 42 | [5 empty] | 7 | [6 empty] | #N/A
|  | 43 | [5 empty] | 8
4KLD003CQ | X 043 03 | 7 | 4KLD003CQ/4LCA301BJ-C-01 | U1000R2V | 7G1.5 | 55 | X 031 03 | 1 | 4LCA301BJ | 24Vcc |  |  | Cooling input of fuel
|  | 17 | [5 empty] | 3 | [6 empty] | #N/A
|  | 45 | [5 empty] | 5
|  | 46 | [5 empty] | 6
| X 251 03 | 36 |  |  |  |  | X 071 03 | 1 | [6 empty] | #N/A
|  | 37 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 045 16 | 3 | 4KLD003CQ/4LCA301BJ-C-02 | U1000R2V | 3G1.5 | 55 | X 031 06 | 2 | 4LCA301BJ | 24Vcc |  | 3rd floor to outside |  |  | WCC 14
|  | 7 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 214 10 | 5 | 4KLD003CQ/4LCA301BJ-C-03 | U1000R2V | 5G1.5 | 55 | X 041 03 | 1 | 4LCA301BJ | 230Vac |  | 3rd floor to outside |  |  | WCC 14
|  | 9 | [5 empty] | 3
|  | 48 | [5 empty] | 5
|  | 49 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 044 03 | 4 | 4KLD003CQ/4LCA301BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 55 | X 051 03 | 1 | 4LCA301BJ | 24Vcc |  |  | Cooling input of fuel
|  | 14 | [5 empty] | 3 | [6 empty] | #N/A
|  | 15 | [5 empty] | 4
|  | 16 | [5 empty] | 5
|  | 17 | [5 empty] | 6 | [6 empty] | #N/A
| X 044 05 | 2 | [5 empty] | 7
|  | 11 | [5 empty] | 12
|  | 16 | [5 empty] | 13 | [6 empty] | #N/A
| X 251 03 | 40 |  |  |  |  | X 071 03 | 5
|  | 41 | [5 empty] | 6
|  | 42 | [5 empty] | 7 | [6 empty] | #N/A
|  | 43 | [5 empty] | 8
|  | 44 | [5 empty] | 9
|  | 45 | [5 empty] | 10 | [6 empty] | #N/A
|  | 46 | [5 empty] | 11
|  | 47 | [5 empty] | 12
4KLD003CQ | X 043 05 | 6 | 4KLD003CQ/4LCA302BJ-C-01 | U1000R2V | 12G1.5 | 40 | X 031 03 | 1 | 4LCA302BJ | 24Vcc |  |  | Fuel feeding system |  | #N/A
|  | 16 | [5 empty] | 6
|  | 32 | [5 empty] | 11
|  | 33 | [5 empty] | 12 | [6 empty] | #N/A
|  | 34 | [5 empty] | 13
|  | 35 | [5 empty] | 14
|  | 36 | [5 empty] | 15 | [6 empty] | #N/A
| X 251 03 | 51 |  |  |  |  | X 071 03 | 4
|  | 52 | [5 empty] | 5
|  | 53 | [5 empty] | 6 | [6 empty] | #N/A
|  | 54 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 130 03 | 7 | 4KLD003CQ/4LCA302BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 40 | X 061 03 | 1 | 4LCA302BJ | 24Vcc |  |  | Fuel feeding system |  | #N/A
|  | 8 | [5 empty] | 2
| X 131 03 | 1 | [5 empty] | 3
|  | 2 | [5 empty] | 4 | [6 empty] | #N/A
|  | 3 | [5 empty] | 5
|  | 4 | [5 empty] | 6
| X 045 05 | 6 |  |  |  |  | X 051 03 | 1 | [6 empty] | #N/A
|  | 16 | [5 empty] | 3
|  | 17 | [5 empty] | 4
| X 045 07 | 2 | [5 empty] | 5 | [6 empty] | #N/A
|  | 9 | [5 empty] | 8
|  | 13 | [5 empty] | 9
|  | 14 | [5 empty] | 10 | [6 empty] | #N/A
| X 251 03 | 48 |  |  |  |  | X 071 03 | 1
|  | 49 | [5 empty] | 2
|  | 50 | [5 empty] | 3 | [6 empty] | #N/A
4KLD003CQ | X 043 03 | 8 | 4KLD003CQ/4LCA401BJ-C-01 | U1000R2V | 7G1.5 | 85 | X 031 03 | 1 | 4LCA401BJ | 24Vcc |  |  | Cooling input of fuel
|  | 18 | [5 empty] | 3
|  | 47 | [5 empty] | 5 | [6 empty] | #N/A
|  | 48 | [5 empty] | 6
| X 251 03 | 55 |  |  |  |  | X 071 03 | 1
|  | 56 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 214 10 | 6 | 4KLD003CQ/4LCA401BJ-C-02 | U1000R2V | 5G1.5 | 85 | X 041 03 | 1 | 4LCA401BJ | 230Vac |  | 3rd floor to outside
|  | 10 | [5 empty] | 3 | [6 empty] | #N/A
|  | 70 | [5 empty] | 5
|  | 71 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 044 05 | 5 | 4KLD003CQ/4LCA401BJ-M-01 | 04IP09EISF BU | 4x2x0.88 | 85 | X 051 03 | 1 | 4LCA401BJ | 24Vcc |  |  | Cooling input of fuel
|  | 17 | [5 empty] | 3
| X 251 03 | 59 |  |  |  |  | X 071 03 | 5 | [6 empty] | #N/A
|  | 60 | [5 empty] | 6
|  | 61 | [5 empty] | 7
|  | 62 | [5 empty] | 8 | [6 empty] | #N/A
|  | 63 | [5 empty] | 9
|  | 64 | [5 empty] | 10
4KLD003CQ | X 043 03 | 9 | 4KLD003CQ/4LCA402BJ-C-01 | U1000R2V | 7G1.5 | 43 | X 031 05 | 1 | 4LCA402BJ | 24Vcc |  |  | Flue gas |  | WCC 14
|  | 19 | [5 empty] | 3
|  | 49 | [5 empty] | 5
| X 251 03 | 65 |  |  |  |  | X 071 03 | 1 | [6 empty] | #N/A
|  | 66 | [5 empty] | 2
|  | 67 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 045 16 | 4 | 4KLD003CQ/4LCA402BJ-C-02 | U1000R2V | 3G1.5 | 43 | X 031 03 | 3 | 4LCA402BJ | 24Vcc |  | 3rd floor to outside
|  | 8 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 044 05 | 6 | 4KLD003CQ/4LCA402BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 43 | X 051 03 | 1 | 4LCA402BJ | 24Vcc |  |  | Flue gas
|  | 18 | [5 empty] | 2
| X 044 07 | 2 | [5 empty] | 3 | [6 empty] | #N/A
|  | 11 | [5 empty] | 6
|  | 12 | [5 empty] | 7
|  | 13 | [5 empty] | 8 | [6 empty] | #N/A
|  | 14 | [5 empty] | 9
|  | 15 | [5 empty] | 10
| X 131 03 | 5 |  |  |  |  | X 061 03 | 1 | [6 empty] | #N/A
|  | 6 | [5 empty] | 2
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4 | [6 empty] | #N/A
| X 251 03 | 68 |  |  |  |  | X 071 03 | 4
|  | 69 | [5 empty] | 5
|  | 70 | [5 empty] | 6 | [6 empty] | #N/A
|  | 71 | [5 empty] | 7
4KLD003CQ | X 043 03 | 10 | 4KLD003CQ/4LCA702BJ-C-01 | U1000R2V | 12G1.5 | 105 | X 031 03 | 1 | 4LCA702BJ | 24Vcc |  |  | Flue gas
|  | 20 | [5 empty] | 3 | [6 empty] | #N/A
|  | 50 | [5 empty] | 5
|  | 51 | [5 empty] | 6
| X 045 12 | 17 |  |  |  |  | X 041 03 | 3 | [6 empty] | #N/A
|  | 7 | [5 empty] | 1
|  | 18 | [5 empty] | 4
| X 251 03 | 72 |  |  |  |  | X 071 03 | 1 | [6 empty] | #N/A
|  | 73 | [5 empty] | 2
|  | 74 | [5 empty] | 3
|  | 75 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 044 07 | 4 | 4KLD003CQ/4LCA702BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 105 | X 051 03 | 1 | 4LCA702BJ | 24Vcc |  |  | Flue gas
|  | 16 | [5 empty] | 5 | [6 empty] | #N/A
|  | 17 | [5 empty] | 6
|  | 18 | [5 empty] | 7
|  | 19 | [5 empty] | 8 | [6 empty] | #N/A
| X 044 09 | 2 | [5 empty] | 9
|  | 7 | [5 empty] | 17
|  | 8 | [5 empty] | 18 | [6 empty] | #N/A
|  | 9 | [5 empty] | 19
|  | 10 | [5 empty] | 20
|  | 11 | [5 empty] | 21 | [6 empty] | #N/A
|  | 12 | [5 empty] | 22
|  | 13 | [5 empty] | 23
|  | 14 | [5 empty] | 24 | [6 empty] | #N/A
| X 044 12 | 2 | [5 empty] | 25
|  | 7 | [5 empty] | 33
4KLD003CQ | X 044 12 | 8 | 4KLD003CQ/4LCA702BJ-M-02 | 12IP09EISF | 12x2x0.88 | 105 | X 051 03 | 34 | 4LCA702BJ | 24Vcc |  | 3rd floor to outside |  |  | WCC 30
|  | 9 | [5 empty] | 35
|  | 10 | [5 empty] | 36
|  | 11 | [5 empty] | 37 | [6 empty] | #N/A
|  | 12 | [5 empty] | 38
|  | 13 | [5 empty] | 39
|  | 14 | [5 empty] | 40 | [6 empty] | #N/A
|  | 2 | [5 empty] | 41
|  | 7 | [5 empty] | 49
|  | 8 | [5 empty] | 50 | [6 empty] | #N/A
|  | 9 | [5 empty] | 51
|  | 10 | [5 empty] | 52
|  | 11 | [5 empty] | 53 | [6 empty] | #N/A
|  | 12 | [5 empty] | 54
|  | 13 | [5 empty] | 55
|  | 14 | [5 empty] | 56 | [6 empty] | #N/A
|  | 1 | [5 empty] | 1
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3 | [6 empty] | #N/A
|  | 4 | [5 empty] | 4
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6 | [6 empty] | #N/A
|  | 92 | [5 empty] | 6
|  | 93 | [5 empty] | 7
4KLD003CQ | X 044 16 | 2 | 4KLD003CQ/4LCA702BJ-M-03 | 08IP09EISF | 8x2x0.88 | 105 | X 051 03 | 57 | 4LCA702BJ | 24Vcc |  | 3rd floor to outside |  |  | WCC 26
|  | 9 | [5 empty] | 61
|  | 10 | [5 empty] | 62
|  | 11 | [5 empty] | 63 | [6 empty] | #N/A
|  | 12 | [5 empty] | 64
|  | 94 | [5 empty] | 71
|  | 95 | [5 empty] | 72 | [6 empty] | #N/A
|  | 96 | [5 empty] | 8
|  | 97 | [5 empty] | 9
|  | 98 | [5 empty] | 10 | [6 empty] | #N/A
|  | 99 | [5 empty] | 11
|  | 100 | [5 empty] | 12
|  | 101 | [5 empty] | 13 | [6 empty] | #N/A
|  | 102 | [5 empty] | 14
|  | 103 | [5 empty] | 15
|  | 104 | [5 empty] | 16 | [6 empty] | #N/A
4KLD003CQ | X 043 03 | 11 | 4KLD003CQ/4LCA802BJ-C-01 | U1000R2V | 12G1.5 | 85 | X 031 03 | 1 | 4LCA802BJ | 24Vcc |  |  | Water steam
|  | 21 | [5 empty] | 5
|  | 52 | [5 empty] | 9 | [6 empty] | #N/A
|  | 53 | [5 empty] | 10
| X 045 12 | 19 |  |  |  |  | X 041 03 | 5
|  | 8 | [5 empty] | 1 | [6 empty] | #N/A
|  | 20 | [5 empty] | 6
| X 251 03 | 89 |  |  |  |  | X 071 03 | 1
|  | 90 | [5 empty] | 2 | [6 empty] | #N/A
|  | 91 | [5 empty] | 3
|  | 92 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD003CQ | X 044 16 | 4 | 4KLD003CQ/4LCA802BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 85 | X 051 03 | 1 | 4LCA802BJ | 24Vcc |  |  | Water steam
|  | 13 | [5 empty] | 5
|  | 14 | [5 empty] | 6 | [6 empty] | #N/A
|  | 15 | [5 empty] | 7
|  | 16 | [5 empty] | 8
| X 045 03 | 2 | [5 empty] | 9 | [6 empty] | #N/A
|  | 7 | [5 empty] | 17
|  | 8 | [5 empty] | 18
|  | 9 | [5 empty] | 19 | [6 empty] | #N/A
|  | 10 | [5 empty] | 20
|  | 11 | [5 empty] | 21
|  | 12 | [5 empty] | 22 | [6 empty] | #N/A
|  | 13 | [5 empty] | 23
|  | 14 | [5 empty] | 24
| X 045 05 | 2 | [5 empty] | 25 | [6 empty] | #N/A
|  | 10 | [5 empty] | 28
|  | 11 | [5 empty] | 29
|  | 15 | [5 empty] | 30 | [6 empty] | #N/A
| X 132 03 | 7 |  |  |  |  | X 061 03 | 1
|  | 8 | [5 empty] | 2
| X 133 03 | 1 | [5 empty] | 3 | [6 empty] | #N/A
|  | 2 | [5 empty] | 4
|  | 3 | [5 empty] | 5
|  | 4 | [5 empty] | 6 | [6 empty] | #N/A
4KLD003CQ | X 133 03 | 5 | 4KLD003CQ/4LCA802BJ-M-02 | 08IP09EISF | 8x2x0.88 | 85 | X 061 03 | 7 | 4LCA802BJ | 24Vcc |  | 3rd floor to outside
|  | 6 | [5 empty] | 8
|  | 7 | [5 empty] | 9 | [6 empty] | #N/A
|  | 8 | [5 empty] | 10
|  | 1 | [5 empty] | 11
|  | 2 | [5 empty] | 12 | [6 empty] | #N/A
|  | 3 | [5 empty] | 13
|  | 4 | [5 empty] | 14
|  | 110 | [5 empty] | 6 | [6 empty] | #N/A
|  | 111 | [5 empty] | 7
|  | 112 | [5 empty] | 8
|  | 113 | [5 empty] | 9 | [6 empty] | #N/A
|  | 114 | [5 empty] | 10
|  | 115 | [5 empty] | 11
|  | 116 | [5 empty] | 12 | [6 empty] | #N/A
|  | 117 | [5 empty] | 13
4KLD003CQ | X 042 16 | 3 | 4KLD003CQ/4LMA001AR-C-01 | U1000R2V | 27G1.5 | 20 | X 074 04 | 9 | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor
|  | 8 | [5 empty] | 13 | [6 empty] | #N/A
|  | 9 | [5 empty] | 14
|  | 10 | [5 empty] | 15
|  | 11 | [5 empty] | 16 | [6 empty] | #N/A
|  | 12 | [5 empty] | 17
|  | 13 | [5 empty] | 18
|  | 14 | [5 empty] | 19 | [6 empty] | #N/A
|  | 15 | [5 empty] | 20
|  | 16 | [5 empty] | 21
|  | 17 | [5 empty] | 22 | [6 empty] | #N/A
18
|  | 19 | [5 empty] | 23
|  | 20 | [5 empty] | 24 | [6 empty] | #N/A
|  | 21 | [5 empty] | 25
|  | 22 | [5 empty] | 26
|  | 23 | [5 empty] | 27 | [6 empty] | #N/A
|  | 4 | [5 empty] | 28
|  | 24 | [5 empty] | 29
|  | 25 | [5 empty] | 30 | [6 empty] | #N/A
|  | 26 | [5 empty] | 31
|  | 27 | [5 empty] | 32
|  | 28 | [5 empty] | 33 | [6 empty] | #N/A
|  | 29 | [5 empty] | 34
|  | 30 | [5 empty] | 35
|  | 31 | [5 empty] | 36 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD003CQ | X 042 16 | 32 | 4KLD003CQ/4LMA001AR-C-02 | U1000R2V | 7G1.5 | 20 | X 074 04 | 33 | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor
|  | 33 | [5 empty] | 34 | [6 empty] | #N/A
|  | 34 | [5 empty] | 35
|  | 35 | [5 empty] | 36
[7 empty] | X? | [7 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 05 | 7 | 4KLD004CQ/4CTE065BJ-C-01 | U1000R2V | 7G1.5 | 67.1 | X? | ?? | 4CTE065BJ | 24Vcc |  |  | Water steam |  | WCC 14
|  | 15 | [5 empty] | ??
|  | 32 | [5 empty] | ??
|  | 33 |  |  |  |  | X 031 02 | ?? | [6 empty] | #N/A
| X 045 09 | 16 |  |  |  |  | X?? | 2
|  | 7 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ | X 043 05 | 8 | 4KLD004CQ/4CTE066BJ-C-01 | U1000R2V | 7G1.5 | 67.1 | X? | ?? | 4CTE066BJ | 24Vcc |  |  | Water steam
|  | 16 | [5 empty] | ??
|  | 34 | [5 empty] | ?? | [6 empty] | #N/A
|  | 35 | [5 empty] | ??
| X 045 09 | 17 |  |  |  |  | X?? | 2
|  | 8 | [5 empty] | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 05 | 6 | 4KLD004CQ/4KIT003AR-C-01 | U1000R2V | 7G1.5 | 10 | X 241 02 | 1 | 4KIT003AR | 24Vcc |  |  | Water steam
|  | 14 | [5 empty] | 3 | [6 empty] | #N/A
|  | 41 | [5 empty] | 3
|  | 42 | [5 empty] | 4
|  | 43 | [5 empty] | 7 | [6 empty] | #N/A
|  | 44 | [5 empty] | 8
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 07 | 3 | 4KLD004CQ/4KIT003AR-C-02 | U1000R2V | 12G1.5 | 10 | X 242 02 | 1 | 4KIT003AR | 24Vcc |  | 3rd floor |  |  | #N/A
|  | 13 | [5 empty] | 2
|  | 21 | [5 empty] | 3
|  | 22 | [5 empty] | 4 | [6 empty] | #N/A
|  | 23 | [5 empty] | 5
|  | 24 | [5 empty] | 6
|  | 25 | [5 empty] | 7 | [6 empty] | #N/A
|  | 26 | [5 empty] | 10
|  | 27 | [5 empty] | 11
|  | 84 | [12 empty] | #N/A
85
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 241 02 | 1 | 4KLD004CQ/4KLC001AR-C-01 | U1000R2V | 12G1.5 | 20 | X 043 07 | 7 | 4KLC001AR | 24Vcc |  |  | Primary air system |  | #N/A
|  | 3 | [5 empty] | 43
|  | 4 | [5 empty] | 44
|  | 5 | [5 empty] | 45 | [6 empty] | #N/A
|  | 6 | [5 empty] | 46
|  | 7 | [5 empty] | 47
|  | 8 | [5 empty] | 48 | [6 empty] | #N/A
| X 251 03 | 44 |  |  |  |  | X 251 03 | 88
|  | 45 | [5 empty] | 89
|  | 46 | [5 empty] | 90 | [6 empty] | #N/A
|  | 47 | [5 empty] | 91
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 03 | 4 | 4KLD004CQ/4LCA101BJ-C-01 | U1000R2V | 7G1.5 | 47 | X 031 03 | 1 | 4LCA101BJ | 24Vcc |  |  | Hydraulic cylinder |  | WCC 14
|  | 10 | [5 empty] | 13
|  | 23 | [5 empty] | 25
|  | 24 | [5 empty] | 26 | [6 empty] | #N/A
|  | 25 | [5 empty] | 27
|  | 26 | [5 empty] | 28
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ | X 043 03 | 27 | 4KLD004CQ/4LCA101BJ-C-02 | U1000R2V | 12G1.5 | 47 | X 031 03 | 29 | 4LCA101BJ | 24Vcc |  | 3rd floor to outside
|  | 28 | [5 empty] | 30
|  | 29 | [5 empty] | 31 | [6 empty] | #N/A
|  | 30 | [5 empty] | 32
|  | 31 | [5 empty] | 33
|  | 32 | [5 empty] | 34 | [6 empty] | #N/A
|  | 7 | [5 empty] | 1
|  | 8 | [5 empty] | 2
|  | 9 | [5 empty] | 3 | [6 empty] | #N/A
|  | 10 | [5 empty] | 4
|  | 11 | [5 empty] | 5
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ | X 214 10 | 3 | 4KLD004CQ/4LCA101BJ-C-03 | U1000R2V | 5G1.5 | 47 | X 041 03 | 1 | 4LCA101BJ | 230Vac |  | 3rd floor to outside
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6 | [6 empty] | #N/A
|  | 11 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 129 03 | 1 | 4KLD004CQ/4LCA101BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 47 | X 061 03 | 1 | 4LCA101BJ | 24Vcc |  |  | Hydraulic cylinder |  | #N/A
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
|  | 4 | [5 empty] | 4 | [6 empty] | #N/A
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6
|  | 7 | [5 empty] | 7 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
| X 130 03 | 1 | [5 empty] | 9
|  | 2 | [5 empty] | 10 | [6 empty] | #N/A
|  | 3 | [5 empty] | 11
|  | 4 | [5 empty] | 12
|  | 5 | [5 empty] | 13 | [6 empty] | #N/A
|  | 6 | [5 empty] | 14
|  | 7 | [5 empty] | 15
|  | 8 | [5 empty] | 16 | [6 empty] | #N/A
| X 251 03 | 6 |  |  |  |  | X 071 03 | 2
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4 | [6 empty] | #N/A
|  | 9 | [5 empty] | 5
|  | 10 | [5 empty] | 6
|  | 11 | [5 empty] | 7 | [6 empty] | #N/A
|  | 12 | [5 empty] | 8
|  | 13 | [5 empty] | 9
4KLD004CQ | X 043 03 | 5 | 4KLD004CQ/4LCA201BJ-C-01 | U1000R2V | 7G1.5 | 88 | X 031 03 | 1 | 4LCA201BJ | 24Vcc |  |  | Thermal water treatment |  | WCC 14
|  | 11 | [5 empty] | 5
|  | 34 | [5 empty] | 10
|  | 35 | [5 empty] | 11 | [6 empty] | #N/A
| X 251 03 | 14 |  |  |  |  | X 071 03 | 1
|  | 15 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ | X 043 09 | 2 | 4KLD004CQ/4LCA201BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 88 | X 051 03 | 1 | 4LCA201BJ | 24Vcc |  |  | Thermal water treatment
|  | 9 | [5 empty] | 3
|  | 10 | [5 empty] | 4 | [6 empty] | #N/A
| X 131 03 | 1 |  |  |  |  | X 061 03 | 1
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3 | [6 empty] | #N/A
|  | 4 | [5 empty] | 4
| X 251 03 | 16 |  |  |  |  | X 071 03 | 3
|  | 17 | [5 empty] | 4 | [6 empty] | #N/A
|  | 18 | [5 empty] | 5
|  | 19 | [5 empty] | 6
|  | 20 | [5 empty] | 7 | [6 empty] | #N/A
|  | 21 | [5 empty] | 8
|  | 22 | [5 empty] | 9
|  | 23 | [5 empty] | 10 | [6 empty] | #N/A
|  | 24 | [5 empty] | 11
4KLD004CQ | X 043 03 | 6 | 4KLD004CQ/4LCA202BJ-C-01 | U1000R2V | 12G1.5 | 58 | X 031 03 | 1 | 4LCA202BJ | 24Vcc |  |  | Grate cooling system module 2-3
|  | 12 | [5 empty] | 7 | [6 empty] | #N/A
|  | 37 | [5 empty] | 13
|  | 38 | [5 empty] | 14
|  | 39 | [5 empty] | 15 | [6 empty] | #N/A
|  | 40 | [5 empty] | 16
|  | 41 | [5 empty] | 17
|  | 42 | [5 empty] | 18 | [6 empty] | #N/A
| X 251 03 | 25 |  |  |  |  | X 071 03 | 1
|  | 26 | [5 empty] | 2
|  | 27 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 09 | 4 | 4KLD004CQ/4LCA202BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 58 | X 051 03 | 1 | 4LCA202BJ | 24Vcc |  |  | Grate cooling system module 2-3
|  | 11 | [5 empty] | 7 | [6 empty] | #N/A
|  | 12 | [5 empty] | 8
|  | 13 | [5 empty] | 9
|  | 14 | [5 empty] | 10 | [6 empty] | #N/A
|  | 15 | [5 empty] | 11
|  | 16 | [5 empty] | 12
| X 043 12 | 2 | [5 empty] | 13 | [6 empty] | #N/A
|  | 9 | [5 empty] | 16
|  | 10 | [5 empty] | 17
|  | 11 | [5 empty] | 18 | [6 empty] | #N/A
| X 131 03 | 5 |  |  |  |  | X 061 03 | 1
|  | 6 | [5 empty] | 2
|  | 7 | [5 empty] | 3 | [6 empty] | #N/A
|  | 8 | [5 empty] | 4
| X 251 03 | 28 |  |  |  |  | X 071 03 | 4
|  | 29 | [5 empty] | 5 | [6 empty] | #N/A
|  | 30 | [5 empty] | 6
|  | 31 | [5 empty] | 7
|  | 32 | [5 empty] | 8 | [6 empty] | #N/A
|  | 33 | [5 empty] | 9
|  | 34 | [5 empty] | 10
|  | 35 | [5 empty] | 11 | [6 empty] | #N/A
|  | 36 | [5 empty] | 12
4KLD004CQ | X 043 03 | 7 | 4KLD004CQ/4LCA203BJ-C-01 | U1000R2V | 12G1.5 | 50 | X 031 03 | 1 | 4LCA203BJ | 24Vcc |  |  | Primary air system
|  | 13 | [5 empty] | 4 | [6 empty] | #N/A
|  | 43 | [5 empty] | 7
|  | 44 | [5 empty] | 8
|  | 45 | [5 empty] | 9 | [6 empty] | #N/A
| X 043 05 | 3 | [5 empty] | 10
|  | 11 | [5 empty] | 20
|  | 17 | [5 empty] | 30 | [6 empty] | #N/A
|  | 18 | [5 empty] | 31
|  | 19 | [5 empty] | 32
|  | 20 | [5 empty] | 33 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 05 | 21 | 4KLD004CQ/4LCA203BJ-C-02 | U1000R2V | 12G1.5 | 83 | X 031 03 | 34 | 4LCA203BJ | 24Vcc |  | 3rd floor to outside
|  | 22 | [5 empty] | 35 | [6 empty] | #N/A
|  | 23 | [5 empty] | 36
|  | 24 | [5 empty] | 37
|  | 25 | [5 empty] | 38 | [6 empty] | #N/A
|  | 46 | [5 empty] | 1
|  | 47 | [5 empty] | 2
|  | 48 | [5 empty] | 3 | [6 empty] | #N/A
|  | 49 | [5 empty] | 4
|  | 50 | [5 empty] | 5
|  | 51 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 043 12 | 4 | 4KLD004CQ/4LCA203BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 50 | X 051 03 | 1 | 4LCA203BJ | 24Vcc |  |  | Primary air system
|  | 12 | [5 empty] | 6 | [6 empty] | #N/A
|  | 13 | [5 empty] | 7
|  | 14 | [5 empty] | 8
|  | 15 | [5 empty] | 9 | [6 empty] | #N/A
|  | 16 | [5 empty] | 10
| X 043 14 | 2 | [5 empty] | 11
|  | 7 | [5 empty] | 19 | [6 empty] | #N/A
|  | 8 | [5 empty] | 20
|  | 9 | [5 empty] | 21
|  | 10 | [5 empty] | 22 | [6 empty] | #N/A
|  | 11 | [5 empty] | 23
|  | 12 | [5 empty] | 24
|  | 13 | [5 empty] | 25 | [6 empty] | #N/A
|  | 14 | [5 empty] | 26
| X 043 16 | 2 | [5 empty] | 27
|  | 9 | [5 empty] | 28 | [6 empty] | #N/A
| X 251 03 | 38 |  |  |  |  | X 071 03 | 2
|  | 39 | [5 empty] | 3
|  | 40 | [5 empty] | 4 | [6 empty] | #N/A
|  | 41 | [5 empty] | 5
|  | 42 | [5 empty] | 6
|  | 49 | [5 empty] | 7 | [6 empty] | #N/A
|  | 50 | [5 empty] | 8
4KLD004CQ | X 043 16 | 4 | 4KLD004CQ/4LCA205BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 75 | X 051 03 | 1 | 4LCA205BJ | 24Vcc |  |  | Primary air system
|  | 10 | [5 empty] | 8 | [6 empty] | #N/A
|  | 11 | [5 empty] | 9
|  | 12 | [5 empty] | 10
|  | 13 | [5 empty] | 11 | [6 empty] | #N/A
|  | 14 | [5 empty] | 12
|  | 15 | [5 empty] | 13
|  | 16 | [5 empty] | 14 | [6 empty] | #N/A
| X 044 03 | 2 | [5 empty] | 15
|  | 9 | [5 empty] | 22
|  | 10 | [5 empty] | 23 | [6 empty] | #N/A
|  | 11 | [5 empty] | 24
|  | 12 | [5 empty] | 25
|  | 13 | [5 empty] | 26 | [6 empty] | #N/A
|  | 14 | [5 empty] | 27
|  | 15 | [5 empty] | 28
4KLD004CQ | X 132 03 | 1 | 4KLD004CQ/4LCA205BJ-M-02 | 08IP09EISF | 8x2x0.88 | 75 | X 061 03 | 1 | 4LCA205BJ | 24Vcc |  | 3rd floor to outside | Primary air system |  | WCC 26
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
|  | 4 | [5 empty] | 4 | [6 empty] | #N/A
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6
|  | 7 | [5 empty] | 7 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
|  | 1 | [5 empty] | 9
|  | 2 | [5 empty] | 10 | [6 empty] | #N/A
|  | 57 | [5 empty] | 1
|  | 58 | [5 empty] | 2
|  | 59 | [5 empty] | 3 | [6 empty] | #N/A
|  | 60 | [5 empty] | 4
|  | 61 | [5 empty] | 5
|  | 62 | [5 empty] | 6 | [6 empty] | #N/A
4KLD004CQ | X 043 05 | 4 | 4KLD004CQ/4LCA403BJ-C-01 | U1000R2V | 7G1.5 | 90 | X 031 06 | 1 | 4LCA403BJ | 24Vcc |  |  | Primary air system
|  | 12 | [5 empty] | 4
|  | 28 | [5 empty] | 7 | [6 empty] | #N/A
| X 251 03 | 51 |  |  |  |  | X 071 03 | 1
|  | 52 | [5 empty] | 2
|  | 53 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 045 14 | 2 | 4KLD004CQ/4LCA403BJ-C-02 | U1000R2V | 3G1.5 | 90 | X 031 03 | 3 | 4LCA403BJ | 24Vcc |  | 3rd floor to outside
|  | 5 | [5 empty] | 7 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 044 03 | 4 | 4KLD004CQ/4LCA403BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 90 | X 051 03 | 1 | 4LCA403BJ | 24Vcc |  |  | Primary air system
|  | 16 | [5 empty] | 2 | [6 empty] | #N/A
| X 044 05 | 2 | [5 empty] | 3
|  | 7 | [5 empty] | 11
|  | 8 | [5 empty] | 4 | [6 empty] | #N/A
|  | 9 | [5 empty] | 12
|  | 10 | [5 empty] | 12
|  | 11 | [5 empty] | 13 | [6 empty] | #N/A
|  | 12 | [5 empty] | 14
|  | 13 | [5 empty] | 15
|  | 14 | [5 empty] | 16 | [6 empty] | #N/A
|  | 15 | [5 empty] | 17
| X 044 07 | 2 | [5 empty] | 18
|  | 10 | [5 empty] | 19 | [6 empty] | #N/A
|  | 11 | [5 empty] | 24
|  | 12 | [5 empty] | 20
| X 044 14 | 3 | [5 empty] | 22 | [6 empty] | #N/A
|  | 15 | [5 empty] | 35
|  | 16 | [5 empty] | 35
| X 251 03 | 54 |  |  |  |  | X 071 03 | 5 | [6 empty] | #N/A
|  | 56 | [5 empty] | 6
|  | 55 | [5 empty] | 6
|  | 57 | [5 empty] | 7 | [6 empty] | #N/A
|  | 58 | [5 empty] | 8
4KLD004CQ | X 044 07 | 3 | 4KLD004CQ/4LCA501BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 71 | X 051 03 | 1 | 4LCA501BJ | 24Vcc |  |  | Water steam
|  | 13 | [5 empty] | 6 | [6 empty] | #N/A
|  | 14 | [5 empty] | 7
|  | 15 | [5 empty] | 8
|  | 16 | [5 empty] | 9 | [6 empty] | #N/A
|  | 17 | [5 empty] | 10
| X 133 03 | 3 |  |  |  |  | X 061 03 | 1
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 59 |  |  |  |  | X 071 03 | 1
|  | 60 | [5 empty] | 2
|  | 61 | [5 empty] | 3 | [6 empty] | #N/A
|  | 62 | [5 empty] | 4
|  | 63 | [5 empty] | 5
|  | 64 | [5 empty] | 6 | [6 empty] | #N/A
|  | 65 | [5 empty] | 7
|  | 66 | [5 empty] | 8
4KLD004CQ | X 133 03 | 5 | 4KLD004CQ/4LCA501BJ-M-02 | 08IP09EISF | 8x2x0.88 | 71 | X 061 03 | 3 | 4LCA501BJ | 24Vcc |  | 3rd floor to outside |  |  | WCC 26
|  | 6 | [5 empty] | 4
|  | 7 | [5 empty] | 5
|  | 8 | [5 empty] | 6 | [6 empty] | #N/A
|  | 1 | [5 empty] | 7
|  | 2 | [5 empty] | 8
|  | 3 | [5 empty] | 9 | [6 empty] | #N/A
|  | 4 | [5 empty] | 10
|  | 5 | [5 empty] | 11
|  | 6 | [5 empty] | 12 | [6 empty] | #N/A
|  | 7 | [5 empty] | 13
|  | 8 | [5 empty] | 14
|  | 1 | [5 empty] | 15 | [6 empty] | #N/A
|  | 2 | [5 empty] | 16
|  | 3 | [5 empty] | 17
|  | 4 | [5 empty] | 18 | [6 empty] | #N/A
4KLD004CQ | X 044 07 | 5 | 4KLD004CQ/4LCA601BJ-M-01 | 08IP09EISF BU | 8x2x0.88 | 58 | X 051 03 | 1 | 4LCA601BJ | 24Vcc |  |  | Flue gas
|  | 18 | [5 empty] | 2
| X 044 09 | 2 | [5 empty] | 3 | [6 empty] | #N/A
|  | 9 | [5 empty] | 8
|  | 10 | [5 empty] | 9
|  | 11 | [5 empty] | 10 | [6 empty] | #N/A
|  | 12 | [5 empty] | 11
|  | 13 | [5 empty] | 12
| X 135 03 | 5 |  |  |  |  | X 061 03 | 1 | [6 empty] | #N/A
|  | 6 | [5 empty] | 2
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4 | [6 empty] | #N/A
| X 251 03 | 67 |  |  |  |  | X 071 03 | 1
|  | 68 | [5 empty] | 2
|  | 69 | [5 empty] | 3 | [6 empty] | #N/A
|  | 70 | [5 empty] | 4
4KLD004CQ | X 043 05 | 5 | 4KLD004CQ/4LCA701BJ-C-01 | U1000R2V | 7G1.5 | 82 | X 031 03 | 1 | 4LCA701BJ | 24Vcc |  |  | Flue gas
|  | 13 | [5 empty] | 2 | [6 empty] | #N/A
|  | 29 | [5 empty] | 3
| X 045 09 | 6 |  |  |  |  | X 041 03 | 1
|  | 15 | [5 empty] | 2 | [6 empty] | #N/A
| X 251 03 | 71 |  |  |  |  | X 071 03 | 1
| PE | PE |  |  |  |  | PE | PE
4KLD004CQ | X 044 09 | 4 | 4KLD004CQ/4LCA701BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 82 | X 051 03 | 1 | 4LCA701BJ | 24Vcc |  |  | Flue gas |  | #N/A
|  | 16 | [5 empty] | 6
| X 044 12 | 2 | [5 empty] | 7
|  | 7 | [5 empty] | 15 | [6 empty] | #N/A
|  | 8 | [5 empty] | 16
|  | 9 | [5 empty] | 17
|  | 10 | [5 empty] | 18 | [6 empty] | #N/A
|  | 11 | [5 empty] | 19
|  | 12 | [5 empty] | 20
|  | 13 | [5 empty] | 21 | [6 empty] | #N/A
|  | 14 | [5 empty] | 22
| X 044 14 | 2 | [5 empty] | 23
|  | 9 | [5 empty] | 30 | [6 empty] | #N/A
|  | 12 | [5 empty] | 33
|  | 13 | [5 empty] | 34
|  | 14 | [5 empty] | 35 | [6 empty] | #N/A
| X 251 03 | 72 |  |  |  |  | X 071 03 | 2
|  | 73 | [5 empty] | 3
|  | 74 | [5 empty] | 4 | [6 empty] | #N/A
|  | 75 | [5 empty] | 5
|  | 76 | [5 empty] | 6
|  | 77 | [5 empty] | 7 | [6 empty] | #N/A
|  | 78 | [5 empty] | 8
|  | 79 | [5 empty] | 9
4KLD004CQ | X 136 03 | 1 | 4KLD004CQ/4LCA701BJ-M-02 | 08IP09EISF | 8x2x0.88 | 82 | X 061 03 | 1 | 4LCA701BJ | 24Vcc |  | 3rd floor to outside |  |  | WCC 26
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
|  | 4 | [5 empty] | 4 | [6 empty] | #N/A
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6
|  | 7 | [5 empty] | 7 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
|  | 1 | [5 empty] | 9
|  | 2 | [5 empty] | 10 | [6 empty] | #N/A
|  | 3 | [5 empty] | 11
|  | 4 | [5 empty] | 12
|  | 80 | [5 empty] | 10 | [6 empty] | #N/A
|  | 81 | [5 empty] | 11
|  | 82 | [5 empty] | 12
|  | 83 | [5 empty] | 13 | [6 empty] | #N/A
4KLD004CQ | X 042 16 | 3 | 4KLD004CQ/4LMA001AR-C-01 | U1000R2V | 27G1.5 | 28 | X 070 04 | 1 | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor
|  | 8 | [5 empty] | 6
|  | 9 | [5 empty] | 7 | [6 empty] | #N/A
|  | 10 | [5 empty] | 8
|  | 11 | [5 empty] | 9
|  | 12 | [5 empty] | 10 | [6 empty] | #N/A
|  | 13 | [5 empty] | 11
|  | 14 | [5 empty] | 12
|  | 15 | [5 empty] | 13 | [6 empty] | #N/A
|  | 16 | [5 empty] | 14
|  | 17 | [5 empty] | 15
|  | 18 | [12 empty] | #N/A
|  | 19 | [5 empty] | 16
|  | 20 | [5 empty] | 17
|  | 21 | [5 empty] | 18 | [6 empty] | #N/A
|  | 22 | [5 empty] | 19
|  | 23 | [5 empty] | 20
|  | 4 | [5 empty] | 21 | [6 empty] | #N/A
|  | 24 | [5 empty] | 22
|  | 25 | [5 empty] | 23
|  | 26 | [5 empty] | 24 | [6 empty] | #N/A
|  | 27 | [5 empty] | 25
|  | 28 | [5 empty] | 26
|  | 29 | [5 empty] | 27 | [6 empty] | #N/A
|  | 30 | [5 empty] | 28
|  | 31 | [5 empty] | 29
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ | X 042 16 | 32 | 4KLD004CQ/4LMA001AR-C-02 | U1000R2V | 12G1.5 | 28 | X 070 04 | 30 | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor
|  | 33 | [5 empty] | 31
|  | 34 | [5 empty] | 32 | [6 empty] | #N/A
|  | 35 | [5 empty] | 1
|  | 36 | [5 empty] | 2
|  | 37 | [5 empty] | 3 | [6 empty] | #N/A
|  | 38 | [5 empty] | 4
#N/A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD004CQ |  |  | 4KLD004CQ/WP3-S-01 |  |  | 19 | KF 301 03 | -X1 P2 | WP3 | 24Vcc |  |  | Pneumatic rapping system
4KLD004CQ |  |  | 4KLD004CQ/WP3-S-02 |  |  | 19 | KF 302 03 | -X1 P2 | WP3 | 24Vcc |  |  | Pneumatic rapping system
4KLD005CQ | KF 301 03 | -X1 P1 | 4KLD005CQ/4KLD001CQ-S-01 | Fiber optic |  | 40 | KF 301 03 | -X1 P2 | 4KLD001CQ | 24Vcc |  |  | Chemical dosing station |  | #N/A
4KLD005CQ | KF 302 03 | -X1 P1 | 4KLD005CQ/4KLD001CQ-S-02 | Fiber optic |  | 40 | KF 302 03 | -X1 P2 | 4KLD001CQ | 24Vcc |  |  | Chemical dosing station
4KLD005CQ | X 042 14 | 3 | 4KLD005CQ/4LCA901BJ-C-01 | U1000R2V | 12G1.5 | 250 | X 031 03 | 1 | 4LCA901BJ | 24Vcc |  |  | Condensate system
|  | 14 | [5 empty] | 9 | [6 empty] | #N/A
|  | 22 | [5 empty] | 17
|  | 23 | [5 empty] | 18
|  | 24 | [5 empty] | 19 | [6 empty] | #N/A
|  | 25 | [5 empty] | 20
| X 043 16 | 15 |  |  |  |  | X 041 03 | 1
|  | 9 | [5 empty] | 5 | [6 empty] | #N/A
|  | 16 | [5 empty] | 6
| X 251 03 | 1 |  |  |  |  | X 071 03 | 1
|  | 2 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD005CQ | X 042 16 | 2 | 4KLD005CQ/4LCA901BJ-M-01 | 12IP09EISF BU | 12x2x0.88 | 250 | X 051 03 | 1 | 4LCA901BJ | 24Vcc |  |  | Condensate system
|  | 13 | [5 empty] | 9 | [6 empty] | #N/A
|  | 15 | [5 empty] | 11
|  | 14 | [5 empty] | 10
|  | 16 | [5 empty] | 12 | [6 empty] | #N/A
|  | 17 | [5 empty] | 13
|  | 18 | [5 empty] | 14
|  | 19 | [5 empty] | 15 | [6 empty] | #N/A
|  | 20 | [5 empty] | 16
| X 043 03 | 2 | [5 empty] | 17
|  | 13 | [5 empty] | 25 | [6 empty] | #N/A
|  | 14 | [5 empty] | 26
|  | 15 | [5 empty] | 27
|  | 16 | [5 empty] | 28 | [6 empty] | #N/A
|  | 17 | [5 empty] | 29
|  | 18 | [5 empty] | 30
|  | 19 | [5 empty] | 31 | [6 empty] | #N/A
|  | 20 | [5 empty] | 32
| X 043 05 | 2 | [5 empty] | 33
|  | 13 | [5 empty] | 41 | [6 empty] | #N/A
|  | 14 | [5 empty] | 42
|  | 15 | [5 empty] | 43
|  | 16 | [5 empty] | 44 | [6 empty] | #N/A
|  | 17 | [5 empty] | 45
4KLD005CQ | X 043 05 | 18 | 4KLD005CQ/4LCA901BJ-M-02 | 12IP09EISF | 12x2x0.88 | 250 | X 051 03 | 46 | 4LCA901BJ | 24Vcc |  | ABR | Condensate system
|  | 19 | [5 empty] | 47 | [6 empty] | #N/A
|  | 20 | [5 empty] | 48
|  | 2 | [5 empty] | 49
|  | 13 | [5 empty] | 55 | [6 empty] | #N/A
|  | 14 | [5 empty] | 56
|  | 15 | [5 empty] | 57
|  | 16 | [5 empty] | 58 | [6 empty] | #N/A
|  | 17 | [5 empty] | 59
|  | 18 | [5 empty] | 60
|  | 7 | [5 empty] | 61 | [6 empty] | #N/A
|  | 17 | [5 empty] | 63
|  | 18 | [5 empty] | 64
|  | 1 | [5 empty] | 1 | [6 empty] | #N/A
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
|  | 4 | [5 empty] | 4 | [6 empty] | #N/A
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6
|  | 7 | [5 empty] | 7 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
|  | 1 | [5 empty] | 9
|  | 2 | [5 empty] | 10 | [6 empty] | #N/A
|  | 3 | [5 empty] | 3
4KLD005CQ | X 042 14 | 4 | 4KLD005CQ/ABR-C-01 | U1000R2V | 12G1.5 | 250 | X? | A | ABR | 24Vcc |  |  | HP steam
|  | 15 | [5 empty] | A | [6 empty] | #N/A
|  | 33 | [5 empty] | A
|  | 34 | [5 empty] | A
|  | 35 | [5 empty] | A | [6 empty] | #N/A
|  | 36 | [5 empty] | A
|  | 37 | [5 empty] | A
|  | 38 | [5 empty] | A | [6 empty] | #N/A
|  | 39 | [5 empty] | A
|  | 40 | [5 empty] | A
|  | 41 | [5 empty] | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD005CQ | X 042 14 | 42 | 4KLD005CQ/ABR-C-02 | U1000R2V | 5G1.5 | 250 | X? | A | ABR | 24Vcc |  | ABR | HP steam
|  | 43 | [5 empty] | A | [6 empty] | #N/A
|  | 4 | [5 empty] | A
|  | 5 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD005CQ | X 120 02 | 3 | 4KLD005CQ/ABR-C-03 | U1000R2V | 12G1.5 | 250 | X? | A | ABR | 24Vcc |  | ABR | HP steam
|  | 4 | [5 empty] | A
|  | 5 | [5 empty] | A | [6 empty] | #N/A
|  | 6 | [5 empty] | A
|  | 7 | [5 empty] | A
|  | 8 | [5 empty] | A | [6 empty] | #N/A
|  | 9 | [5 empty] | A
|  | 10 | [5 empty] | A
|  | 6 | [5 empty] | A | [6 empty] | #N/A
|  | 7 | [5 empty] | A
|  | 8 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD005CQ | X 220 02 | 1 | 4KLD005CQ/ABR-C-04 | U1000R2V | 27G1.5 | 250 | X? | A | ABR | 24Vcc |  | ABR | HP steam
|  | 2 | [5 empty] | A
|  | 3 | [5 empty] | A | [6 empty] | #N/A
|  | 4 | [5 empty] | A
|  | 5 | [5 empty] | A
|  | 6 | [5 empty] | A | [6 empty] | #N/A
|  | 7 | [5 empty] | A
|  | 8 | [5 empty] | A
|  | 9 | [5 empty] | A | [6 empty] | #N/A
|  | 10 | [5 empty] | A
|  | 11 | [5 empty] | A
|  | 12 | [5 empty] | A | [6 empty] | #N/A
|  | 13 | [5 empty] | A
|  | 14 | [5 empty] | A
|  | 15 | [5 empty] | A | [6 empty] | #N/A
|  | 16 | [5 empty] | A
|  | 17 | [5 empty] | A
|  | 18 | [5 empty] | A | [6 empty] | #N/A
|  | 19 | [5 empty] | A
|  | 20 | [5 empty] | A
|  | 21 | [5 empty] | A | [6 empty] | #N/A
|  | 22 | [5 empty] | A
|  | 23 | [5 empty] | A
|  | 24 | [5 empty] | A | [6 empty] | #N/A
|  | A |  |  |  |  | X 251 03 | 9
|  | A | [5 empty] | 10
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD005CQ | X 120 22 | 1 | 4KLD005CQ/ABR-C-05 | U1000R2V | 5G1.5 | 250 | X? | A | ABR | 24Vcc |  | ABR | HP steam
|  | 2 | [5 empty] | A
|  | 17 | [5 empty] | A | [6 empty] | #N/A
|  | 18 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLD005CQ | X 043 07 | 8 | 4KLD005CQ/ABR-M-01 | 08IP09EISF BU | 8x2x0.88 | 250 | X? | A | ABR | 24Vcc |  |  | HP steam |  | #N/A
|  | 19 | [5 empty] | A
|  | 20 | [5 empty] | A
| X 043 09 | 2 | [5 empty] | A | [6 empty] | #N/A
|  | 11 | [5 empty] | A
|  | 12 | [5 empty] | A
|  | 13 | [5 empty] | A | [6 empty] | #N/A
|  | 14 | [5 empty] | A
| X 105 03 | 3 | [5 empty] | A
|  | 4 | [5 empty] | A | [6 empty] | #N/A
|  | 5 | [5 empty] | A
|  | 6 | [5 empty] | A
|  | 7 | [5 empty] | A | [6 empty] | #N/A
|  | 8 | [5 empty] | A
| X 106 03 | 1 | [5 empty] | A
|  | 2 | [5 empty] | A | [6 empty] | #N/A
4KLD005CQ | X 106 03 | 3 | 4KLD005CQ/ABR-M-02 | 08IP09EISF | 8x2x0.88 | 250 | X? | A | ABR | 24Vcc |  | ABR | HP steam
|  | 4 | [5 empty] | A
|  | 5 | [5 empty] | A | [6 empty] | #N/A
|  | 6 | [5 empty] | A
|  | 7 | [5 empty] | A
|  | 8 | [5 empty] | A | [6 empty] | #N/A
|  | 1 | [5 empty] | A
|  | 2 | [5 empty] | A
|  | 11 | [5 empty] | A | [6 empty] | #N/A
|  | 12 | [5 empty] | A
|  | 13 | [5 empty] | A
|  | 14 | [5 empty] | A | [6 empty] | #N/A
|  | 15 | [5 empty] | A
|  | 16 | [5 empty] | A
|  | 17 | [5 empty] | A | [6 empty] | #N/A
|  | 18 | [5 empty] | A
4KLD006CQ | X 042 12 | 5 | 4KLD006CQ/4LGA000DJ-C-01 | U1000R2V | 7G1.5 | 10 | X? | A | 4LGA000DJ | 24Vcc
|  | 26 | [5 empty] | A | [6 empty] | #N/A
|  | 27 | [5 empty] | A
|  | 28 | [5 empty] | A
|  | 29 | [5 empty] | A | [6 empty] | #N/A
|  | 30 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLD006CQ | X 042 09 | 3 | 4KLD006CQ/4LGA001DJ-C-01 | U1000R2V | 7G1.5 | 10 | X? | A | 4LGA001DJ | 24Vcc |  |  |  |  | WCC 14
|  | 11 | [5 empty] | A
|  | 12 | [5 empty] | A
|  | 13 | [5 empty] | A | [6 empty] | #N/A
|  | 14 | [5 empty] | A
| X 251 03 | 1 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD006CQ | X 042 09 | 4 | 4KLD006CQ/4LGA002DJ-C-01 | U1000R2V | 7G1.5 | 10 | X? | A | 4LGA002DJ | 24Vcc
|  | 15 | [5 empty] | A
|  | 16 | [5 empty] | A | [6 empty] | #N/A
|  | 17 | [5 empty] | A
|  | 18 | [5 empty] | A
| X 251 03 | 2 | [5 empty] | A | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4KLD006CQ | X 042 09 | 5 | 4KLD006CQ/4LGA003DJ-C-01 | U1000R2V | 7G1.5 | 10 | X? | A | 4LGA003DJ | 24Vcc
|  | 19 | [5 empty] | A | [6 empty] | #N/A
|  | 20 | [5 empty] | A
| X 251 03 | 3 | [5 empty] | A
|  | 4 | [5 empty] | A | [6 empty] | #N/A
|  | 5 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE
4KLD006CQ | X 042 09 | 6 | 4KLD006CQ/4LGA004DJ-C-01 | U1000R2V | 7G1.5 | 10 | X? | A | 4LGA004DJ | 24Vcc |  |  |  |  | WCC 14
|  | 21 | [5 empty] | A
|  | 22 | [5 empty] | A
|  | 23 | [5 empty] | A | [6 empty] | #N/A
| X 251 03 | 6 | [5 empty] | A
|  | 7 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD006CQ | X 042 09 | 7 | 4KLD006CQ/4LGA005DJ-C-01 | U1000R2V | 12G1.5 | 10 | X? | A | 4LGA005DJ | 24Vcc
|  | 24 | [5 empty] | A
|  | 25 | [5 empty] | A | [6 empty] | #N/A
|  | 26 | [5 empty] | A
|  | 27 | [5 empty] | A
|  | 28 | [5 empty] | A | [6 empty] | #N/A
| X 042 12 | 3 | [5 empty] | A
|  | 15 | [5 empty] | A
|  | 16 | [5 empty] | A | [6 empty] | #N/A
|  | 17 | [5 empty] | A
| X 251 03 | 10 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD006CQ | X 042 12 | 4 | 4KLD006CQ/4LGA006DJ-C-01 | U1000R2V | 12G1.5 | 10 | X? | A | 4LGA006DJ | 24Vcc
|  | 18 | [5 empty] | A
|  | 19 | [5 empty] | A | [6 empty] | #N/A
|  | 20 | [5 empty] | A
|  | 21 | [5 empty] | A
|  | 22 | [5 empty] | A | [6 empty] | #N/A
|  | 23 | [5 empty] | A
|  | 24 | [5 empty] | A
|  | 25 | [5 empty] | A | [6 empty] | #N/A
| X 251 03 | 13 | [5 empty] | A
|  | 14 | [5 empty] | A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4KLD006CQ | X 042 09 | 6 | 4KLD006CQ/4LGA004DJ-C-02 | U1000R2V | 7G1.5 | 10 |  |  | 4LGA004DJ | 24Vcc |  | HV ROOM
21
|  | 22 | [12 empty] | #N/A
23
6
|  | 7 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 051 03 | 1 | 4LCA001BJ/4CRF100PDT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF100PDT | + | 4CRF100PDT | 24Vcc |  | JB to instrument | Cooling water system
|  | 9 | [5 empty] | - | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 2 | 4LCA001BJ/4CRF182PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF182PT | 1 | 4CRF182PT | 24Vcc |  | JB to instrument | Cooling water system
|  | 10 | [5 empty] | 2
4LCA001BJ | X 051 03 | 3 | 4LCA001BJ/4CRF200PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF200PT | 1 | 4CRF200PT | 24Vcc |  | JB to instrument | Cooling water system |  | #N/A
|  | 11 | [5 empty] | 2
4LCA001BJ | X 051 03 | 4 | 4LCA001BJ/4CRF202TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF202TT | + | 4CRF202TT | 24Vcc |  | JB to instrument | Cooling water system
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 6 | 4LCA001BJ/4CRF421FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF421FT | A+ | 4CRF421FT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 14 | [5 empty] | A
4LCA001BJ | X 051 03 | 7 | 4LCA001BJ/4CRF465FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF465FT | A+ | 4CRF465FT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 15 | [5 empty] | A
4LCA001BJ | X 051 03 | 8 | 4LCA001BJ/4CRF496FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF496FT | A+ | 4CRF496FT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 16 | [5 empty] | A | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 17 | 4LCA001BJ/4CRF540FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF540FT | + | 4CRF540FT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 21 | [5 empty] | -
4LCA001BJ | X 051 03 | 5 | 4LCA001BJ/4CRF587FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF587FT | A+ | 4CRF587FT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 13 | [5 empty] | A
4LCA001BJ | X 031 03 | 1 | 4LCA001BJ/4DEM038LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM038LCV | 1 | 4DEM038LCV | 24Vcc |  | JB to instrument | Ash removal system
|  | 14 | [5 empty] | 2 | [6 empty] | #N/A
|  | 21 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 041 03 | 1 | 4LCA001BJ/4DEM038LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM038LCV | x2 | 4DEM038LCV | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 5 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA001BJ | X 031 03 | 8 | 4LCA001BJ/4DEM053ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM053ZT | 13 | 4DEM053ZT | 24Vcc |  | JB to instrument | Ash removal system
|  | 28 | [5 empty] | 14
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 031 03 | 7 | 4LCA001BJ/4DEM054ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM054ZT | 13 | 4DEM054ZT | 24Vcc |  | JB to instrument | Ash removal system
|  | 27 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 031 03 | 2 | 4LCA001BJ/4DEM086LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM086LCV | 1 | 4DEM086LCV | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 15 | [5 empty] | 2
|  | 22 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA001BJ | X 041 03 | 2 | 4LCA001BJ/4DEM086LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM086LCV | x2 | 4DEM086LCV | 24Vcc |  | JB to instrument | Ash removal system
|  | 6 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 031 03 | 10 | 4LCA001BJ/4DEM091ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM091ZT | 13 | 4DEM091ZT | 24Vcc |  | JB to instrument | Ash removal system
|  | 30 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 031 03 | 9 | 4LCA001BJ/4DEM092ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM092ZT | 13 | 4DEM092ZT | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 29 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA001BJ | X 031 03 | 11 | 4LCA001BJ/4FFB009ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 58 | 4FFB009ZS | A1 | 4FFB009ZS | 24Vcc |  | JB to instrument | Ash removal system
|  | 20 | [5 empty] | A2
|  | 31 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001BJ | X 051 03 | 27 | 4LCA001BJ/4FGOFIT563-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4FGOFIT563 | + | 4FGOFIT563 | 24Vcc |  | JB to instrument | Ash removal system
|  | 32 | [5 empty] | - | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 25 | 4LCA001BJ/4FTA067PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA067PT | + | 4FTA067PT | 24Vcc |  | JB to instrument | Flue gas
|  | 30 | [5 empty] | -
4LCA001BJ | X 051 03 | 18 | 4LCA001BJ/4SAR009PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR009PT | + | 4SAR009PT | 24Vcc |  | JB to instrument | Pneumatic system |  | #N/A
|  | 22 | [5 empty] | -
4LCA001BJ | X 051 03 | 20 | 4LCA001BJ/4SAR030PSAL-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR030PSAL | + | 4SAR030PSAL | 24Vcc |  | JB to instrument | Pneumatic system
|  | 24 | [5 empty] | - | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 26 | 4LCA001BJ/4SAR044PSAL-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR044PSAL | + | 4SAR044PSAL | 24Vcc |  | JB to instrument | Pneumatic system
|  | 31 | [5 empty] | -
4LCA001BJ | X 031 03 | 3 | 4LCA001BJ/4SEO203LSHH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4SEO203LSHH | 1 | 4SEO203LSHH | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 16 | [5 empty] | 2
|  | 23 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA001BJ | X 051 03 | 19 | 4LCA001BJ/4SEO260LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO260LT | + | 4SEO260LT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 23 | [5 empty] | -
4LCA001CR | X 041 05 | 1 | 4LCA001CR/4EPA055VAR-C-01 | U1000R2V | 3G2.5 | 12 | X 041 05 | 1 | 4EPA055VAR | 24Vcc | ALIMENTATION DU VFD POMPE EAU ALIMENTAIRE 1 | 1st floor | Thermal water treatment |  | WCC 14
|  | 2 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LCA001CR | X 041 05 | 1 | 4LCA001CR/4EPA075VAR-C | U1000R2V | 3G2.5 | 12 | X 041 05 | 1 | 4EPA075VAR | 24Vcc | ALIMENTATION DU VFD POMPE EAU ALIMENTAIRE 2 | 1st floor | Thermal water treatment |  | WCC 14
|  | 2 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LCA001CR | X 041 05 | 1 | 4LCA001CR/4FAF065VAR-C | U1000R2V | 3G2.5 | 12 | X 021 08 | 1 | 4FAF065VAR | 24Vcc | ALIMENTATION DU VFD VENTILATEUR D'AIR PRIMAIRE | 1st floor | Primary air system |  | WCC 14
|  | 2 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA001CR | X 041 05 | 1 | 4LCA001CR/4FTA049VAR-C | U1000R2V | 3G2.5 | 12 | X 021 10 | 1 | 4FTA049VAR | 24Vcc | ALIMENTATION DU VFD PVENTILATEUR DE RECYCLAGE DES FUMÉES | 1st floor | Flue gas recirculation system |  | WCC 14
|  | 2 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA001CR | X 041 05 | 1 | 4LCA001CR/4KCL999CQ-C-01 | U1000R2V | 5G1.5 | 35 | X 022 05 | 1 | 4KCL999CQ | 24Vcc | ALIMENTATION DU VFD VENTILATEUR D'AIR DU BRÛLEUR 1 & 2 | 1st floor | Burner system |  | #N/A
|  | 2 | [5 empty] | 3
| X 041 09 | 1 |  |  |  |  | X 022 08 | 1
|  | 2 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA001CR | X 041 13 | 1 | 4LCA001CR/4KCL999CQ-C-02 | U1000R2V | 3G1.5 | 35 | X 021 16 | 1 | 4KCL999CQ | 24Vcc | ALIMENTATION DU VFD VENTILATEUR D'AIR SECONDAIRE | 1st floor | Secondary air system
|  | 2 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 16 | 4LCA002BJ/4DEM035LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM035LSL | L+ | 4DEM035LSL | 24Vcc |  | JB to instrument | Ash removal system
|  | 26 | [5 empty] | L- | [6 empty] | #N/A
|  | 36 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 17 | 4LCA002BJ/4DEM036LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM036LSH | L+ | 4DEM036LSH | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 27 | [5 empty] | L-
|  | 37 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA002BJ | X 031 03 | 18 | 4LCA002BJ/4DEM039LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM039LSL | L+ | 4DEM039LSL | 24Vcc |  | JB to instrument | Ash removal system
|  | 28 | [5 empty] | L-
|  | 38 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 19 | 4LCA002BJ/4DEM040LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM040LSH | L+ | 4DEM040LSH | 24Vcc |  | JB to instrument | Ash removal system
|  | 29 | [5 empty] | L- | [6 empty] | #N/A
|  | 39 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 20 | 4LCA002BJ/4DEM064LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM064LSL | L+ | 4DEM064LSL | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 30 | [5 empty] | L-
|  | 40 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA002BJ | X 031 03 | 21 | 4LCA002BJ/4DEM065LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM065LSH | L+ | 4DEM065LSH | 24Vcc |  | JB to instrument | Ash removal system
|  | 31 | [5 empty] | L-
|  | 41 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 23 | 4LCA002BJ/4DEM087LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM087LSH | L+ | 4DEM087LSH | 24Vcc |  | JB to instrument | Ash removal system
|  | 33 | [5 empty] | L- | [6 empty] | #N/A
|  | 43 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 22 | 4LCA002BJ/4DEM088LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM088LSL | L+ | 4DEM088LSL | 24Vcc |  | JB to instrument | Ash removal system |  | #N/A
|  | 32 | [5 empty] | L-
|  | 42 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA002BJ | X 061 03 | 3 | 4LCA002BJ/4EBA122LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA122LCV | 6 | 4EBA122LCV | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 4 | [5 empty] | 7
4LCA002BJ | X 031 03 | 1 | 4LCA002BJ/4EPA101ZSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 20 | 4EPA101ZSH | 1 | 4EPA101ZSH | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 6 | [5 empty] | 2
|  | 11 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA002BJ | X 031 03 | 2 | 4LCA002BJ/4EPA101ZSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 20 | 4EPA101ZSL | 1 | 4EPA101ZSL | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 7 | [5 empty] | 2
|  | 12 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 051 03 | 1 | 4LCA002BJ/4EPA102PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA102PT | + | 4EPA102PT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 5 | [5 empty] | - | [6 empty] | #N/A
4LCA002BJ | X 051 03 | 2 | 4LCA002BJ/4EPA103PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA103PT | + | 4EPA103PT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 6 | [5 empty] | -
4LCA002BJ | X 051 03 | 3 | 4LCA002BJ/4EPA108PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA108PT | + | 4EPA108PT | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 7 | [5 empty] | -
4LCA002BJ | X 031 03 | 3 | 4LCA002BJ/4EPA111ZSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 20 | 4EPA111ZSH | 1 | 4EPA111ZSH | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 8 | [5 empty] | 2 | [6 empty] | #N/A
|  | 13 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA002BJ | X 031 03 | 4 | 4LCA002BJ/4EPA111ZSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 20 | 4EPA111ZSL | 1 | 4EPA111ZSL | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 9 | [5 empty] | 2
|  | 14 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA002BJ | X 051 03 | 4 | 4LCA002BJ/4EPA112PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA112PT | + | 4EPA112PT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 8 | [5 empty] | -
4LCA002BJ | X 051 03 | 9 | 4LCA002BJ/4EPA113PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA113PT | + | 4EPA113PT | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 16 | [5 empty] | -
4LCA002BJ | X 051 03 | 10 | 4LCA002BJ/4EPA118PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA118PT | + | 4EPA118PT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 17 | [5 empty] | - | [6 empty] | #N/A
4LCA002BJ | X 051 03 | 11 | 4LCA002BJ/4FTA151TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA151TT | + | 4FTA151TT | 24Vcc |  | JB to instrument | Water steam
|  | 18 | [5 empty] | -
4LCA002BJ | X 061 03 | 1 | 4LCA002BJ/4SEN205TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SEN205TCV | 6 | 4SEN205TCV | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 2 | [5 empty] | 7
4LCA002BJ | X 051 03 | 25 | 4LCA002BJ/4SEO003FQIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO003FQIT | C1 | 4SEO003FQIT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 26 | [5 empty] | C2 | [6 empty] | #N/A
4LCA002BJ | X 051 03 | 13 | 4LCA002BJ/4SEO202TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEN202TT | + | 4SEO202TT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 20 | [5 empty] | -
4LCA002BJ | X 051 03 | 12 | 4LCA002BJ/4SEO203LAH-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO203LAH | + | 4SEO203LAH | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 19 | [5 empty] | -
4LCA002BJ | X 051 03 | 14 | 4LCA002BJ/4SEO203LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO203LT | + | 4SEO203LT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 21 | [5 empty] | - | [6 empty] | #N/A
4LCA002BJ | X 051 03 | 15 | 4LCA002BJ/4SEO204TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO204TT | + | 4SEO204TT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 22 | [5 empty] | -
4LCA002BJ | X 051 03 | 23 | 4LCA002BJ/4SEP002FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SEP002FIT | C1 | 4SEP002FIT | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 24 | [5 empty] | C2
4LCA002CR | X 021 08 | 1 | 4LCA002CR/4LKD007AR-C | U1000R2V | 3G2.5 | 12 | X 531 05 | 1 | 4LKD007AR | 24Vcc |  | 2nd floor
|  | 3 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002CR | X 021 10 | 1 | 4LCA002CR/4LKD007AR-C-02 | U1000R2V | 3G2.5 | 12 | X532 05 | 1 | 4LKD007AR | 24Vcc |  | 2nd floor
|  | 3 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002CR | X 021 12 | 1 | 4LCA002CR/4LKF005AR-C | U1000R2V | 3G2.5 | 12 | X 311 05 | 1 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system
|  | 3 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002CR | X 021 14 | 1 | 4LCA002CR/4LKF005AR-C-02 | U1000R2V | 3G2.5 | 12 | X 312 05 | 1 | 4LKF005AR | 24Vcc |  | 2nd floor | Condensate system
|  | 3 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002CR | X 021 16 | 1 | 4LCA002CR/4LKF006AR-C | U1000R2V | 3G2.5 | 12 | X 531 05 | 1 | 4LKF006AR | 24Vcc |  | 2nd floor
|  | 5 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA002CR | X 021 18 | 1 | 4LCA002CR/4LKF006AR-C-02 | U1000R2V | 3G2.5 | 12 | X 532 05 | 1 | 4LKF006AR | 24Vcc |  | 2nd floor
|  | 5 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 1 | 4LCA101BJ/4DEM034LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM034LCV | 1 | 4DEM034LCV | 24Vcc |  | JB to instrument | Ash removal system
|  | 13 | [5 empty] | 2 | [6 empty] | #N/A
|  | 25 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 041 03 | 1 | 4LCA101BJ/4DEM034LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 0 | x2 | 4DEM034LCV | 230Vca |  | JB to instrument | Ash removal system |  | #N/A
|  | 5 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA101BJ | X 031 03 | 2 | 4LCA101BJ/4DEM063LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM063LCV | 1 | 4DEM063LCV | 24Vcc |  | JB to instrument | Ash removal system
|  | 14 | [5 empty] | 2
|  | 26 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 041 03 | 2 | 4LCA101BJ/4DEM063LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EPA075VAR | x2 | 4DEM063LCV | 230Vca |  | JB to instrument | Ash removal system
|  | 6 | [5 empty] | x1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 061 03 | 5 | 4LCA101BJ/4FAF084HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF084HV | 6 | 4FAF084HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 6 | [5 empty] | 7
4LCA101BJ | X 061 03 | 7 | 4LCA101BJ/4FAF085HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF085HV | 6 | 4FAF085HV | 24Vcc |  | JB to instrument | Primary air system
|  | 8 | [5 empty] | 7 | [6 empty] | #N/A
4LCA101BJ | X 061 03 | 9 | 4LCA101BJ/4FAF086HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF086HV | 6 | 4FAF086HV | 24Vcc |  | JB to instrument | Primary air system
|  | 10 | [5 empty] | 7
4LCA101BJ | X 061 03 | 11 | 4LCA101BJ/4FAF087HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF087HV | 6 | 4FAF087HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 12 | [5 empty] | 7
4LCA101BJ | X 061 03 | 1 | 4LCA101BJ/4FAF107HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF107HV | 6 | 4FAF107HV | 24Vcc |  | JB to instrument | Primary air system
|  | 2 | [5 empty] | 7 | [6 empty] | #N/A
4LCA101BJ | X 061 03 | 3 | 4LCA101BJ/4FAF108HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF108HV | 6 | 4FAF108HV | 24Vcc |  | JB to instrument | Primary air system
|  | 4 | [5 empty] | 7
4LCA101BJ | X 051 03 | 3 | 4LCA101BJ/4FGO003FE-M-01 | 01IP09EGSF BU | 1x2x0.88 | 25 | 4FGO003FE | + | 4FGO003FE | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
|  | 6 | [5 empty] | -
4LCA101BJ | X 031 03 | 9 | 4LCA101BJ/4FGR376ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR376ZT | 1 | 4FGR376ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 21 | [5 empty] | 2 | [6 empty] | #N/A
|  | 33 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 10 | 4LCA101BJ/4FGR377ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR377ZT | 1 | 4FGR377ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
|  | 22 | [5 empty] | 2
|  | 34 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA101BJ | X 031 03 | 7 | 4LCA101BJ/4FGR378ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR378ZT | 1 | 4FGR378ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 19 | [5 empty] | 2
|  | 31 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 8 | 4LCA101BJ/4FGR379ZT-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR379ZT | 1 | 4FGR379ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 20 | [5 empty] | 2 | [6 empty] | #N/A
|  | 32 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 5 | 4LCA101BJ/4FGR380ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR380ZS | 1 | 4FGR380ZS | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
|  | 17 | [5 empty] | 2
|  | 29 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA101BJ | X 031 03 | 6 | 4LCA101BJ/4FGR381ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR381ZS | 1 | 4FGR381ZS | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 18 | [5 empty] | 2
|  | 30 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 3 | 4LCA101BJ/4FGR382ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR382ZS | 1 | 4FGR382ZS | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 15 | [5 empty] | 2 | [6 empty] | #N/A
|  | 27 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA101BJ | X 031 03 | 4 | 4LCA101BJ/4FGR382ZS-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR383ZS | 1 | 4FGR383ZS | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
|  | 16 | [5 empty] | 2
|  | 28 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA101BJ | X 051 03 | 1 | 4LCA101BJ/4FSR201LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR201LT | + | 4FSR201LT | 24Vcc |  | JB to instrument | LFO storage tanks
|  | 4 | [5 empty] | -
4LCA101BJ | X 051 03 | 2 | 4LCA101BJ/4FSR202LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR202LT | + | 4FSR202LT | 24Vcc |  | JB to instrument | LFO storage tanks |  | #N/A
|  | 5 | [5 empty] | -
4LCA101BJ | X 061 03 | 13 | 4LCA101BJ/4FTA047HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA047HV | 6 | 4FTA047HV | 24Vcc |  | JB to instrument | Primary air system
|  | 14 | [5 empty] | 7 | [6 empty] | #N/A
4LCA101BJ | X 061 03 | 15 | 4LCA101BJ/4FTA066HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA066HV | 6 | 4FTA066HV | 24Vcc |  | JB to instrument | Flue gas
|  | 16 | [5 empty] | 7
4LCA101BJ | X 051 03 | 7 | 4LCA101BJ/V2-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | V2 | + | V2 | 24Vcc |  | JB to instrument | Secondary air system |  | #N/A
|  | 9 | [5 empty] | -
4LCA101BJ | X 051 03 | 8 | 4LCA101BJ/V3-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | V3 | + | V3 | 24Vcc |  | JB to instrument | Secondary air system
|  | 10 | [5 empty] | - | [6 empty] | #N/A
4LCA101HSS |  |  | 4LCA101HSS/4LCA102HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA102HSS | 24Vcc |  | JB to instrument
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA102BJ | X 061 03 | 5 | 4LCA102BJ/4EBA007PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA007PCV | 6 | 4EBA007PCV | 24Vcc |  | JB to instrument | Flue gas
|  | 6 | [5 empty] | 7
4LCA102BJ | X 051 03 | 3 | 4LCA102BJ/4EBA028PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA028PT | + | 4EBA028PT | 24Vcc |  | JB to instrument | Condensate system |  | #N/A
|  | 11 | [5 empty] | -
4LCA102BJ | X 051 03 | 4 | 4LCA102BJ/4EBA028TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA028TT | + | 4EBA028TT | 24Vcc |  | JB to instrument | Condensate system
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA102BJ | X 051 03 | 19 | 4LCA102BJ/4FAF220TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF220TT | + | 4FAF220TT | 24Vcc |  | JB to instrument | Primary air system
|  | 22 | [5 empty] | -
4LCA102BJ | X 051 03 | 20 | 4LCA102BJ/4FAF221TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF221TT | + | 4FAF221TT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 23 | [5 empty] | -
4LCA102BJ | X 051 03 | 21 | 4LCA102BJ/4FAF222TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF222TT | + | 4FAF222TT | 24Vcc |  | JB to instrument | Primary air system
|  | 24 | [5 empty] | - | [6 empty] | #N/A
4LCA102BJ | X 061 03 | 1 | 4LCA102BJ/4FSR262TCV-M-02 | 01IP09EGSF | 1x2x0.88 | 12 | 0 | 6 | 4FSR262TCV | 24Vcc |  | JB to instrument | Secondary air system
|  | 2 | [5 empty] | 7
4LCA102BJ | X 051 03 | 1 | 4LCA102BJ/4FTA069PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA069PT | + | 4FTA069PT | 24Vcc |  | JB to instrument | Secondary air system |  | #N/A
|  | 2 | [5 empty] | -
4LCA102BJ | X 061 03 | 7 | 4LCA102BJ/4FVA040FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVA040FCV | 6 | 4FVA040FCV | 24Vcc |  | JB to instrument | Water steam
|  | 8 | [5 empty] | 7 | [6 empty] | #N/A
4LCA102BJ | X 051 03 | 7 | 4LCA102BJ/4SAR205PI-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR205PI | + | 4SAR205PI | 24Vcc |  | JB to instrument | Pneumatic rapping system
|  | 15 | [5 empty] | -
4LCA102BJ | X 051 03 | 8 | 4LCA102BJ/4SAR207FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR207FIT | + | 4SAR207FIT | 24Vcc |  | JB to instrument | Pneumatic rapping system |  | #N/A
|  | 16 | [5 empty] | -
4LCA102BJ | X 051 03 | 9 | 4LCA102BJ/4SAR405PI-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR405PI | + | 4SAR405PI | 24Vcc |  | JB to instrument | Pneumatic rapping system
|  | 17 | [5 empty] | - | [6 empty] | #N/A
4LCA102BJ | X 051 03 | 10 | 4LCA102BJ/4SAR407FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 65 | 4SAR407FIT | + | 4SAR407FIT | 24Vcc |  | JB to instrument | Pneumatic rapping system
|  | 18 | [5 empty] | -
4LCA102BJ | X 051 03 | 6 | 4LCA102BJ/4SEB004FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SEB004FIT | + | 4SEB004FIT | 24Vcc |  | JB to instrument | Wet cleaning system |  | #N/A
|  | 14 | [5 empty] | -
4LCA102BJ | X 061 03 | 3 | 4LCA102BJ/4SEO014XV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO014XV | 6 | 4SEO014XV | 24Vcc |  | JB to instrument | Drain&Vent
|  | 4 | [5 empty] | 7 | [6 empty] | #N/A
4LCA102BJ | X 031 03 | 1 | 4LCA102BJ/4SEO203LSHH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4SEO203LSHH |  | 4SEO203LSHH | 24Vcc |  | JB to instrument | Drain&Vent
7
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA102BJ | X 031 03 | 2 | 4LCA102BJ/4SEO203LSLL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 55 | 4SEO203LSLL |  | 4SEO203LSLL | 24Vcc |  | JB to instrument | Drain&Vent
|  | 8 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA102BJ | X 051 03 | 5 | 4LCA102BJ/4SEO262TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO262TT | + | 4SEO262TT | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 13 | [5 empty] | -
4LCA102BJ | X 051 03 | 25 | 4LCA102BJ/V4-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | V4 | + | V4 | 24Vcc |  | JB to instrument | Pneumatic rapping system
|  | 28 | [5 empty] | - | [6 empty] | #N/A
4LCA102BJ | X 051 03 | 26 | 4LCA102BJ/V5-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | V5 | + | V5 | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 29 | [5 empty] | -
4LCA102BJ | X 051 03 | 27 | 4LCA102BJ/V9-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | V9 | + | V9 | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 30 | [5 empty] | -
4LCA201BJ | X 051 03 | 2 | 4LCA201BJ/4CTE087TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 67.1 | 4CTE087TT | + | 4CTE087TT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 4 | [5 empty] | - | [6 empty] | #N/A
4LCA201BJ | X 051 03 | 1 | 4LCA201BJ/4EBA104TICA-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA104TICA | + | 4EBA104TICA | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 3 | [5 empty] | -
4LCA201BJ | X 031 03 | 2 | 4LCA201BJ/4EBA112LSHH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA112LSHH | 1 | 4EBA112LSHH | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 6 | [5 empty] | 2
|  | 10 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA201BJ | X 031 03 | 3 | 4LCA201BJ/4EBA113LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA113LSH | 1 | 4EBA113LSH | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 7 | [5 empty] | 2
|  | 11 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA201BJ | X 031 03 | 13 | 4LCA201BJ/4EBA114LZLL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA114LZLL | 1 | 4EBA114LZLL | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 15 | [5 empty] | 2 | [6 empty] | #N/A
|  | 17 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA201BJ | X 051 03 | 9 | 4LCA201BJ/4EBA116LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA116LT | + | 4EBA116LT | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 12 | [5 empty] | -
4LCA201BJ | X 051 03 | 10 | 4LCA201BJ/4EBA117LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA117LT | + | 4EBA117LT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 13 | [5 empty] | - | [6 empty] | #N/A
4LCA201BJ | X 051 03 | 11 | 4LCA201BJ/4EBA118LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA118LT | + | 4EBA118LT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 14 | [5 empty] | -
4LCA201BJ | X 061 03 | 1 | 4LCA201BJ/4FSR113LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR113LCV | 6 | 4FSR113LCV | 24Vcc |  | JB to instrument | Thermal water treatment |  | #N/A
|  | 2 | [5 empty] | 7
4LCA201BJ | X 061 03 | 3 | 4LCA201BJ/4SDX103FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 100 | 4SDX103FCV | 6 | 4SDX103FCV | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 4 | [5 empty] | 7 | [6 empty] | #N/A
4LCA201HSS |  |  | 4LCA201HSS/4LCA202HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA202HSS |  |  | JB to instrument | Thermal water treatment
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA202BJ | X 051 03 | 1 | 4LCA202BJ/4CRF431TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF431TT | + | 4CRF431TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 7 | [5 empty] | -
4LCA202BJ | X 051 03 | 2 | 4LCA202BJ/4CRF455TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF455TT | + | 4CRF455TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 8 | [5 empty] | -
4LCA202BJ | X 051 03 | 3 | 4LCA202BJ/4CRF485TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF485TT | + | 4CRF485TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 9 | [5 empty] | - | [6 empty] | #N/A
4LCA202BJ | X 051 03 | 4 | 4LCA202BJ/4CRF492TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF492TT | + | 4CRF492TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 10 | [5 empty] | -
4LCA202BJ | X 051 03 | 5 | 4LCA202BJ/4CRF516TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF516TT | + | 4CRF516TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 11 | [5 empty] | -
4LCA202BJ | X 051 03 | 6 | 4LCA202BJ/4CRF530TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF530TT | + | 4CRF530TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA202BJ | X 051 03 | 13 | 4LCA202BJ/4CRF550TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF550TT | + | 4CRF550TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 16 | [5 empty] | -
4LCA202BJ | X 051 03 | 14 | 4LCA202BJ/4CRF572TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF572TT | + | 4CRF572TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 17 | [5 empty] | -
4LCA202BJ | X 051 03 | 15 | 4LCA202BJ/4CTE088TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 67.1 | 4CTE088TT | + | 4CTE088TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 18 | [5 empty] | - | [6 empty] | #N/A
4LCA202BJ | X 031 03 | 1 | 4LCA202BJ/4FAF184ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF184ZS | A1 | 4FAF184ZS | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 7 | [5 empty] | A2
|  | 13 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA202BJ | X 031 03 | 2 | 4LCA202BJ/4FAF187ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF187ZS | A1 | 4FAF187ZS | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 8 | [5 empty] | A2 | [6 empty] | #N/A
|  | 14 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA202BJ | X 031 03 | 4 | 4LCA202BJ/4FAF216ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF216ZS | A1 | 4FAF216ZS | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 10 | [5 empty] | A2
|  | 16 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA202BJ | X 031 03 | 5 | 4LCA202BJ/4FAF217ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF217ZS | A1 | 4FAF217ZS | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 11 | [5 empty] | A2
|  | 17 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA202BJ | X 031 03 | 6 | 4LCA202BJ/4FAF218ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF218ZS | A1 | 4FAF218ZS | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 12 | [5 empty] | A2 | [6 empty] | #N/A
|  | 18 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA202BJ | X 061 03 | 1 | 4LCA202BJ/4FGR103HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR103HV | 6 | 4FGR103HV | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 2 | [5 empty] | 7
4LCA202BJ | X 061 03 | 3 | 4LCA202BJ/4FGR104HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR104HV | 6 | 4FGR104HV | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 4 | [5 empty] | 7 | [6 empty] | #N/A
4LCA202BJ | X 031 03 | 3 | 4LCA202BJ/4FGR214ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR214ZS | A1 | 4FGR214ZS | 24Vcc |  | JB to instrument | Primary air system
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA202HSS |  |  | 4LCA202HSS/4LCA301HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA301HSS |  |  | JB to instrument | Grate cooling system
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 051 03 | 1 | 4LCA203BJ/4CRF167TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF167TT | + | 4CRF167TT | 24Vcc |  | JB to instrument | Cooling water system
|  | 6 | [5 empty] | - | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 2 | 4LCA203BJ/4CRF168TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF168TT | + | 4CRF168TT | 24Vcc |  | JB to instrument | Cooling water system
|  | 7 | [5 empty] | -
4LCA203BJ | X 051 03 | 3 | 4LCA203BJ/4CRF426TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF426TT | + | 4CRF426TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 8 | [5 empty] | -
4LCA203BJ | X 051 03 | 4 | 4LCA203BJ/4CRF441TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF441TT | + | 4CRF441TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 9 | [5 empty] | - | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 5 | 4LCA203BJ/4CRF447TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF447TT | + | 4CRF447TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 10 | [5 empty] | -
4LCA203BJ | X 051 03 | 11 | 4LCA203BJ/4CRF471TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF471TT | + | 4CRF471TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 19 | [5 empty] | -
4LCA203BJ | X 051 03 | 12 | 4LCA203BJ/4CRF478TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF478TT | + | 4CRF478TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 20 | [5 empty] | - | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 13 | 4LCA203BJ/4CRF502TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF502TT | + | 4CRF502TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 21 | [5 empty] | -
4LCA203BJ | X 051 03 | 14 | 4LCA203BJ/4CRF509TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF509TT | + | 4CRF509TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 22 | [5 empty] | -
4LCA203BJ | X 051 03 | 15 | 4LCA203BJ/4CRF522TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF522TT | + | 4CRF522TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 23 | [5 empty] | - | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 16 | 4LCA203BJ/4CRF544TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF544TT | + | 4CRF544TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 24 | [5 empty] | -
4LCA203BJ | X 051 03 | 17 | 4LCA203BJ/4CRF558TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF558TT | + | 4CRF558TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3 |  | #N/A
|  | 25 | [5 empty] | -
4LCA203BJ | X 051 03 | 18 | 4LCA203BJ/4CRF565TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF565TT | + | 4CRF565TT | 24Vcc |  | JB to instrument | Grate cooling system module 2-3
|  | 26 | [5 empty] | - | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 27 | 4LCA203BJ/4FAF164PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF164PT | + | 4FAF164PT | 24Vcc |  | JB to instrument | Primary air system
|  | 28 | [5 empty] | -
4LCA203BJ | X 031 03 | 1 | 4LCA203BJ/4FAF181ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF181ZS | A1 | 4FAF181ZS | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 4 | [5 empty] | A2
|  | 7 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA203BJ | X 031 03 | 2 | 4LCA203BJ/4FAF182ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF182ZS | A1 | 4FAF182ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 5 | [5 empty] | A2
|  | 8 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 3 | 4LCA203BJ/4FAF183ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF183ZS | A1 | 4FAF183ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 6 | [5 empty] | A2 | [6 empty] | #N/A
|  | 9 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 10 | 4LCA203BJ/4FAF185ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF185ZS | A1 | 4FAF185ZS | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 20 | [5 empty] | A2
|  | 30 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA203BJ | X 031 03 | 11 | 4LCA203BJ/4FAF186ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF186ZS | A1 | 4FAF186ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 21 | [5 empty] | A2
|  | 31 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 12 | 4LCA203BJ/4FAF188ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF188ZS | A1 | 4FAF188ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 22 | [5 empty] | A2 | [6 empty] | #N/A
|  | 32 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 13 | 4LCA203BJ/4FAF190ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF190ZS | A1 | 4FAF190ZS | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 23 | [5 empty] | A2
|  | 33 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA203BJ | X 031 03 | 14 | 4LCA203BJ/4FAF211ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF211ZS | A1 | 4FAF211ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 24 | [5 empty] | A2
|  | 34 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 15 | 4LCA203BJ/4FAF212ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF212ZS | A1 | 4FAF212ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 25 | [5 empty] | A2 | [6 empty] | #N/A
|  | 35 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 16 | 4LCA203BJ/4FAF213ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF213ZS | A1 | 4FAF213ZS | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 26 | [5 empty] | A2
|  | 36 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA203BJ | X 031 03 | 17 | 4LCA203BJ/4FAF215ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF215ZS | A1 | 4FAF215ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 27 | [5 empty] | A2
|  | 37 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 031 03 | 18 | 4LCA203BJ/4FAF219ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FAF219ZS | A1 | 4FAF219ZS | 24Vcc |  | JB to instrument | Primary air system
|  | 28 | [5 empty] | A2 | [6 empty] | #N/A
|  | 38 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA203BJ | X 051 03 | 33 | 4LCA203BJ/4FGR283ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR283ZT | 4 | 4FGR283ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
| X 055 02 | 1 | [5 empty] | 1
|  | 3 | [5 empty] | 3
| X 051 03 | 41 | [5 empty] | 2 | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 34 | 4LCA203BJ/4FGR284ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR284ZT | 4 | 4FGR284ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
| X 055 02 | 2 | [5 empty] | 1
|  | 4 | [5 empty] | 3 | [6 empty] | #N/A
| X 051 03 | 42 | [5 empty] | 2
4LCA203BJ | X 051 03 | 35 | 4LCA203BJ/4FGR285ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR285ZT | 4 | 4FGR285ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
| X 055 02 | 7 | [5 empty] | 1 | [6 empty] | #N/A
|  | 9 | [5 empty] | 3
| X 051 03 | 43 | [5 empty] | 2
4LCA203BJ | X 051 03 | 36 | 4LCA203BJ/4FGR286ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR286ZT | 4 | 4FGR286ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
| X 055 02 | 8 | [5 empty] | 1
|  | 10 | [5 empty] | 3
| X 051 03 | 44 | [5 empty] | 2 | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 37 | 4LCA203BJ/4FGR287ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR287ZT | 4 | 4FGR287ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
| X 055 02 | 13 | [5 empty] | 1
|  | 15 | [5 empty] | 3 | [6 empty] | #N/A
| X 051 03 | 45 | [5 empty] | 2
4LCA203BJ | X 051 03 | 38 | 4LCA203BJ/4FGR288ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR288ZT | 4 | 4FGR288ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
| X 055 02 | 14 | [5 empty] | 1 | [6 empty] | #N/A
|  | 16 | [5 empty] | 3
| X 051 03 | 46 | [5 empty] | 2
4LCA203BJ | X 051 03 | 39 | 4LCA203BJ/4FGR289ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR289ZT | 4 | 4FGR289ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
| X 055 02 | 19 | [5 empty] | 1
|  | 21 | [5 empty] | 3
| X 051 03 | 47 | [5 empty] | 2 | [6 empty] | #N/A
4LCA203BJ | X 051 03 | 40 | 4LCA203BJ/4FGR290ZT-M-01 | ORIGINAL CABLE | 4x0.5 | 12 | 4FGR290ZT | 4 | 4FGR290ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
| X 055 02 | 20 | [5 empty] | 1
|  | 22 | [5 empty] | 3 | [6 empty] | #N/A
| X 051 03 | 48 | [5 empty] | 2
4LCA204BJ | X 051 04 | 15 | 4LCA204BJ/4EBA001LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA001LT | + | 4EBA001LT | 24Vcc |  | JB to instrument | Condensate system
|  | 20 | [5 empty] | - | [6 empty] | #N/A
4LCA204BJ | X 051 04 | 14 | 4LCA204BJ/4EBA001PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA001PT | + | 4EBA001PT | 24Vcc |  | JB to instrument | Condensate system
|  | 19 | [5 empty] | -
4LCA204BJ | X 061 03 | 9 | 4LCA204BJ/4EBA005LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA005LCV | 6 | 4EBA005LCV | 24Vcc |  | JB to instrument | Condensate system |  | #N/A
|  | 10 | [5 empty] | 7
4LCA204BJ | X 051 04 | 11 | 4LCA204BJ/4EBA106PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA106PT | + | 4EBA106PT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 16 | [5 empty] | - | [6 empty] | #N/A
4LCA204BJ | X 061 03 | 1 | 4LCA204BJ/4EBA134UV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA134UV | 6 | 4EBA134UV | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 2 | [5 empty] | 7
4LCA204BJ | X 051 02 | 1 | 4LCA204BJ/4FAF061FT-C-01 | U1000R2V | 3G1.5 | 12 | 4FAF061FT | 1 | 4FAF061FT | 24Vcc |  | JB to instrument | Primary air system |  | WCC 14
|  | 4 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LCA204BJ | X 051 04 | 1 | 4LCA204BJ/4FAF061FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF061FT | 26 | 4FAF061FT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 6 | [5 empty] | 27
4LCA204BJ | X 051 04 | 3 | 4LCA204BJ/4FAF071TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF071TT | + | 4FAF071TT | 24Vcc |  | JB to instrument | Primary air system
|  | 8 | [5 empty] | - | [6 empty] | #N/A
4LCA204BJ | X 051 04 | 4 | 4LCA204BJ/4FAF073PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF073PT | + | 4FAF073PT | 24Vcc |  | JB to instrument | Primary air system
|  | 9 | [5 empty] | -
4LCA204BJ | X 051 04 | 2 | 4LCA204BJ/4FAF075PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF075PT | + | 4FAF075PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 7 | [5 empty] | -
4LCA204BJ | X 051 04 | 5 | 4LCA204BJ/4FAF389FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF389FT | 26 | 4FAF389FT | 24Vcc |  | JB to instrument | Primary air system
|  | 10 | [5 empty] | 27 | [6 empty] | #N/A
4LCA204BJ | X 051 04 | 21 | 4LCA204BJ/4SEO001FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO001FIT | + | 4SEO001FIT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 22 | [5 empty] | -
4LCA204BJ | X 051 04 | 13 | 4LCA204BJ/4SEO201LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO201LT | + | 4SEO201LT | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 18 | [5 empty] | -
4LCA204BJ | X 051 04 | 12 | 4LCA204BJ/4SEO201PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO201PT | + | 4SEO201PT | 24Vcc |  | JB to instrument | Drain&Vent
|  | 17 | [5 empty] | - | [6 empty] | #N/A
4LCA204BJ | X 061 03 | 5 | 4LCA204BJ/4SEO225LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO225LCV | 6 | 4SEO225LCV | 24Vcc |  | JB to instrument | Drain&Vent
|  | 6 | [5 empty] | 7
4LCA204BJ | X 061 03 | 7 | 4LCA204BJ/4SVA003PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SVA003PCV | 6 | 4SVA003PCV | 24Vcc |  | JB to instrument | Condensate system |  | #N/A
|  | 8 | [5 empty] | 7
4LCA204BJ | X 061 03 | 3 | 4LCA204BJ/4SVA203PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SVA203PCV | 6 | 4SVA203PCV | 24Vcc |  | JB to instrument | Drain&Vent
|  | 4 | [5 empty] | 7 | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 21 | 4LCA205BJ/4EBA051PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA051PT | + | 4EBA051PT | 24Vcc |  | JB to instrument | Condensate system
|  | 28 | [5 empty] | -
4LCA205BJ | X 051 03 | 7 | 4LCA205BJ/4FAF088PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF088PT | + | 4FAF088PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 14 | [5 empty] | -
4LCA205BJ | X 051 03 | 15 | 4LCA205BJ/4FAF089PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF089PT | + | 4FAF089PT | 24Vcc |  | JB to instrument | Primary air system
|  | 22 | [5 empty] | - | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 16 | 4LCA205BJ/4FAF090PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF090PT | + | 4FAF090PT | 24Vcc |  | JB to instrument | Primary air system
|  | 23 | [5 empty] | -
4LCA205BJ | X 051 03 | 17 | 4LCA205BJ/4FAF091PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF091PT | + | 4FAF091PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 24 | [5 empty] | -
4LCA205BJ | X 051 03 | 18 | 4LCA205BJ/4FAF092PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF092PT | + | 4FAF092PT | 24Vcc |  | JB to instrument | Primary air system
|  | 25 | [5 empty] | - | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 19 | 4LCA205BJ/4FAF093PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF093PT | + | 4FAF093PT | 24Vcc |  | JB to instrument | Primary air system
|  | 26 | [5 empty] | -
4LCA205BJ | X 051 03 | 1 | 4LCA205BJ/4FAF109PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF109PT | + | 4FAF109PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 8 | [5 empty] | -
4LCA205BJ | X 051 03 | 2 | 4LCA205BJ/4FAF110PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF110PT | + | 4FAF110PT | 24Vcc |  | JB to instrument | Primary air system
|  | 9 | [5 empty] | - | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 3 | 4LCA205BJ/4FAF111PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF111PT | + | 4FAF111PT | 24Vcc |  | JB to instrument | Primary air system
|  | 10 | [5 empty] | -
4LCA205BJ | X 051 03 | 4 | 4LCA205BJ/4FAF112PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF112PT | + | 4FAF112PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 11 | [5 empty] | -
4LCA205BJ | X 051 03 | 5 | 4LCA205BJ/4FAF113PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF113PT | + | 4FAF113PT | 24Vcc |  | JB to instrument | Primary air system
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 6 | 4LCA205BJ/4FAF114PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF114PT | + | 4FAF114PT | 24Vcc |  | JB to instrument | Primary air system
|  | 13 | [5 empty] | -
4LCA205BJ | X 061 03 | 9 | 4LCA205BJ/4FGR062HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA062HV | 6 | 4FGR062HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
| X 061 03 | 10 | [5 empty] | 7
4LCA205BJ | X 061 03 | 5 | 4LCA205BJ/4FGR082HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR082HV | 6 | 4FGR082HV | 24Vcc |  | JB to instrument | Primary air system
| X 061 03 | 6 | [5 empty] | 7 | [6 empty] | #N/A
4LCA205BJ | X 061 03 | 7 | 4LCA205BJ/4FGR083HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR083HV | 6 | 4FGR083HV | 24Vcc |  | JB to instrument | Primary air system
| X 061 03 | 8 | [5 empty] | 7
4LCA205BJ | X 061 03 | 1 | 4LCA205BJ/4FGR105HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR105HV | 6 | 4FGR105HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
| X 061 03 | 2 | [5 empty] | 7
4LCA205BJ | X 061 03 | 3 | 4LCA205BJ/4FGR106HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR106HV | 6 | 4FGR106HV | 24Vcc |  | JB to instrument | Primary air system
| X 061 03 | 4 | [5 empty] | 7 | [6 empty] | #N/A
4LCA205BJ | X 051 03 | 20 | 4LCA205BJ/4FTA061FT-M | 01IP09EGSF | 1x2x0.88 | 12 | 4FTA049VAR | + | 4FTA061FT | 24Vcc |  | JB to instrument | Flue gas
|  | 27 | [5 empty] | -
4LCA205BJ | X 051 03 | 20 | 4LCA205BJ/4FTA061TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA061FT | + | 4FTA061TT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
| X 051 03 | 27 | [5 empty] | -
4LCA301BJ | X 051 03 | 1 | 4LCA301BJ/4CRF134PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF134PT | 1 | 4CRF134PT | 24Vcc |  | JB to instrument | Cooling water system
|  | 3 | [5 empty] | 2 | [6 empty] | #N/A
4LCA301BJ | X 051 03 | 2 | 4LCA301BJ/4CRF166PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF166PT | 1 | 4CRF166PT | 24Vcc |  | JB to instrument | Cooling water system
|  | 4 | [5 empty] | 2
4LCA301BJ | X 031 03 | 1 | 4LCA301BJ/4CRF625LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4CRF625LCV | 1 | 4CRF625LCV | 24Vcc |  | JB to instrument | Cooling input of fuel |  | #N/A
|  | 3 | [5 empty] | 2
|  | 5 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA301BJ | X 041 03 | 1 | 4LCA301BJ/4CRF625LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 0 | x2 | 4CRF625LCV | 230Vca |  | JB to instrument | Cooling input of fuel
|  | 3 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA301BJ | X 031 06 | 1 | 4LCA301BJ/4CRF626LS-C-01 | U1000R2V | 3G1.5 | 12 | 4CRF626LS | 1 | 4CRF626LS | 24Vcc |  | JB to instrument | Cooling input of fuel
| X 031 06 | 4 |  |  |  |  | 4CRF626LS | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA301BJ | X 031 03 | 2 | 4LCA301BJ/4CRF626LS-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 0 | 3 | 4CRF626LS | 24Vcc |  | JB to instrument | Cooling input of fuel
|  | 6 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA301BJ | X 051 03 | 7 | 4LCA301BJ/4FGR102FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR102FT | + | 4FGR102FT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 12 | [5 empty] | -
4LCA301BJ | X 031 06 | 2 | 4LCA301BJ/4FGR390FT-C-01 | U1000R2V | 3G1.5 | 12 | 4FGR390FT | 1 | 4FGR390FT | 24Vcc |  | JB to instrument | Primary air system
| X 031 06 | 5 |  |  |  |  | 4FGR390FT | 2 | [6 empty] | #N/A
| X 031 06 | 2 |  |  |  |  | 4FGR390FT | 1
| PE | PE |  |  |  |  | PE | PE
4LCA301BJ | X 051 03 | 5 | 4LCA301BJ/4FGR390FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR390FT | 26 | 4FGR390FT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 6 | [5 empty] | 27
4LCA301BJ | X 051 03 | 8 | 4LCA301BJ/4FSR230FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR230FIT | + | 4FSR230FIT | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 13 | [5 empty] | - | [6 empty] | #N/A
4LCA301HSS |  |  | 4LCA301HSS/4LCA302HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA302HSS |  |  | JB to instrument | Fuel feeding system
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA302BJ | X 061 03 | 5 | 4LCA302BJ/4EBA072PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA072PCV | 6 | 4EBA072PCV | 24Vcc |  | JB to instrument | Condensate system
|  | 6 | [5 empty] | 7
4LCA302BJ | X 031 03 | 1 | 4LCA302BJ/4FGR004ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR004ZS | A1 | 4FGR004ZS | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | 6 | [5 empty] | A2
|  | 11 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA302BJ | X 031 03 | 2 | 4LCA302BJ/4FGR005ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR005ZS | A1 | 4FGR005ZS | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 7 | [5 empty] | A2
|  | 12 | [5 empty] | Y1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA302BJ | X 031 03 | 3 | 4LCA302BJ/4FGR006ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR006ZS | A1 | 4FGR006ZS | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 8 | [5 empty] | A2 | [6 empty] | #N/A
|  | 13 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE
4LCA302BJ | X 031 03 | 4 | 4LCA302BJ/4FGR007ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR007ZS | A1 | 4FGR007ZS | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | 9 | [5 empty] | A2
|  | 14 | [5 empty] | Y1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA302BJ | X 031 03 | 5 | 4LCA302BJ/4FGR008ZS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | X? | B | 4FGR008ZS | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 10 | [5 empty] | B
|  | 15 | [5 empty] | B | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA302BJ | X 051 03 | 1 | 4LCA302BJ/4FGR280ZT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR280ZT | 61 | 4FGR280ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 3 | [5 empty] | 62 | [6 empty] | #N/A
4LCA302BJ | X 051 03 | 2 | 4LCA302BJ/4FGR281ZT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR281ZT | 61 | 4FGR281ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder
|  | 4 | [5 empty] | 62
4LCA302BJ | X 051 03 | 5 | 4LCA302BJ/4FGR282ZT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR282ZT | 61 | 4FGR282ZT | 24Vcc |  | JB to instrument | Hydraulic cylinder |  | #N/A
|  | 8 | [5 empty] | 62
4LCA302BJ | X 061 03 | 1 | 4LCA302BJ/4FSR154PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR154PCV | 6 | 4FSR154PCV | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 2 | [5 empty] | 7 | [6 empty] | #N/A
4LCA302BJ | X 061 03 | 3 | 4LCA302BJ/4FSR162TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR162TCV | 6 | 4FSR162TCV | 24Vcc |  | JB to instrument | Thermal water treatment
|  | 4 | [5 empty] | 7
4LCA302BJ |  | + | 4LCA302BJ/4JDA315TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 6 | 4JDA315TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 9
4LCA302BJ |  | + | 4LCA302BJ/4JDA316TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 15 | 4JDA316TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 28 | [6 empty] | #N/A
4LCA302BJ | X 051 03 | 16 | 4LCA302BJ/4JDA317TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4JDA317TT | + | 4JDA317TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 29 | [5 empty] | -
4LCA302BJ | X 051 03 | 17 | 4LCA302BJ/4JDA318TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4JDA318TT | + | 4JDA318TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | 30 | [5 empty] | -
4LCA302BJ | X 051 03 | 18 | 4LCA302BJ/4JDA319TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4JDA319TT | + | 4JDA319TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 31 | [5 empty] | - | [6 empty] | #N/A
4LCA302BJ |  | + | 4LCA302BJ/4JDA320TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 19 | 4JDA320TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 32
4LCA302BJ |  | + | 4LCA302BJ/4JDA321TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 20 | 4JDA321TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 33
4LCA302BJ |  | + | 4LCA302BJ/4JDA322TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 21 | 4JDA322TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 34 | [6 empty] | #N/A
4LCA302BJ | X 051 03 | 7 | 4LCA302BJ/4JDA323TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4JDA323TT | + | 4JDA323TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | 10 | [5 empty] | -
4LCA302BJ |  | + | 4LCA302BJ/4JDA324TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 22 | 4JDA324TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 35
4LCA302BJ |  | + | 4LCA302BJ/4JDA325TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 23 | 4JDA325TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 36 | [6 empty] | #N/A
4LCA302BJ |  | + | 4LCA302BJ/4JDA326TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 24 | 4JDA326TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 37
4LCA302BJ |  | + | 4LCA302BJ/4JDA327TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 25 | 4JDA327TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 38
4LCA302BJ |  | + | 4LCA302BJ/4JDA328TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 26 | 4JDA328TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 39 | [6 empty] | #N/A
4LCA302BJ |  | + | 4LCA302BJ/4JDA329TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 27 | 4JDA329TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 40
4LCA302BJ |  | + | 4LCA302BJ/4JDA330TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 41 | 4JDA330TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 45
4LCA302BJ |  | + | 4LCA302BJ/4JDA331TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 42 | 4JDA331TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 46 | [6 empty] | #N/A
4LCA302BJ |  | + | 4LCA302BJ/4JDA332TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 43 | 4JDA332TT | 24Vcc |  | JB to instrument | Fuel feeding system
|  | - | [5 empty] | 47
4LCA302BJ |  | + | 4LCA302BJ/4JDA333TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | X 051 03 | 44 | 4JDA333TT | 24Vcc |  | JB to instrument | Fuel feeding system |  | #N/A
|  | - | [5 empty] | 48
4LCA302HSS |  |  | 4LCA302HSS/4LCA401HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA401HSS |  |  | JB to instrument | Fuel feeding system
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA401BJ | X 031 03 | 1 | 4LCA401BJ/4CRF619LCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4CRF619LCV | 1 | 4CRF619LCV | 24Vcc |  | JB to instrument | Cooling input of fuel
|  | 3 | [5 empty] | 2 | [6 empty] | #N/A
|  | 5 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA401BJ | X 041 03 | 1 | 4LCA401BJ/4CRF619LCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | #REF! | x2 | 4CRF619LCV | 230Vac |  | JB to instrument | Cooling input of fuel |  | #N/A
|  | 3 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA401BJ | X 031 07 | 1 | 4LCA401BJ/4CRF620LS-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4CRF620LS | 1 | 4CRF620LS | 24Vcc |  | JB to instrument | Cooling input of fuel
|  | 2 | [5 empty] | 2
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA401BJ | X 051 03 | 1 | 4LCA401BJ/4EBA051PIC-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA051PIC | + | 4EBA051PIC | 24Vcc |  | JB to instrument | Condensate system
|  | 3 | [5 empty] | - | [6 empty] | #N/A
4LCA401HSS |  |  | 4LCA401HSS/4LCA402HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA402HSS |  |  | JB to instrument | Flue gas
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA402BJ | X 031 03 | 1 | 4LCA402BJ/4FGR003LSLL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR003LSLL | 1 | 4FGR003LSLL | 24Vcc |  | JB to instrument | Flue gas
|  | 5 | [5 empty] | 2
|  | 2 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA402BJ | X 031 03 | 1 | 4LCA402BJ/4FGR003LSLL-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM035LSL | 3 | 4FGR003LSLL | 24Vcc |  | JB to instrument | Flue gas
|  | 5 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA402BJ | X 051 03 | 1 | 4LCA402BJ/4FGR101AT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR101AT | + | 4FGR101AT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 2 | [5 empty] | -
4LCA402BJ | X 031 03 | 3 | 4LCA402BJ/4FGR259FT-C-01 | U1000R2V | 3G1.5 | 12 | 4FGR259FT | 1 | 4FGR259FT | 24Vcc |  | JB to instrument | Flue gas
|  | 7 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA402BJ | X 051 03 | 9 | 4LCA402BJ/4FGR259FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR259FT | 26 | 4FGR259FT | 24Vcc |  | JB to instrument | Flue gas
|  | 10 | [5 empty] | 27 | [6 empty] | #N/A
4LCA402BJ | X 061 03 | 1 | 4LCA402BJ/4FGR261HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR261HV | 6 | 4FGR261HV | 24Vcc |  | JB to instrument | Flue gas
|  | 2 | [5 empty] | 7
4LCA402BJ | X 061 03 | 3 | 4LCA402BJ/4FGR262HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR262HV | 6 | 4FGR262HV | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 4 | [5 empty] | 7
4LCA402BJ | X 051 03 | 3 | 4LCA402BJ/4FTA026TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA026TT | + | 4FTA026TT | 24Vcc |  | JB to instrument | Flue gas
|  | 6 | [5 empty] | - | [6 empty] | #N/A
4LCA402BJ | X 051 03 | 4 | 4LCA402BJ/4FTA027TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA027TT | + | 4FTA027TT | 24Vcc |  | JB to instrument | Flue gas
|  | 7 | [5 empty] | -
4LCA402BJ | X 051 03 | 5 | 4LCA402BJ/4FTA059FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA059FT | + | 4FTA059FT | 24Vcc |  | JB to instrument | Fluegas recirculation system |  | #N/A
|  | 8 | [5 empty] | -
4LCA402HSS |  |  | 4LCA402HSS/4LCA501HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA501HSS |  |  | JB to instrument | Flue gas
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA403BJ | X 051 03 | 16 | 4LCA403BJ/4EPA001FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA001FIT | - | 4EPA001FIT | 24Vcc |  | JB to instrument | Water steam
|  | 8 | [5 empty] | + | [6 empty] | #N/A
4LCA403BJ | X 051 03 | 17 | 4LCA403BJ/4EPA001PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA001PT | - | 4EPA001PT | 24Vcc |  | JB to instrument | Water steam
|  | 9 | [5 empty] | +
4LCA403BJ | X 051 03 | 10 | 4LCA403BJ/4EPA002PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA002PT | + | 4EPA002PT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 18 | [5 empty] | -
4LCA403BJ | X 051 03 | 4 | 4LCA403BJ/4FAF078FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF078FT | + | 4FAF078FT | 24Vcc |  | JB to instrument | Primary air system
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA403BJ | X 051 03 | 5 | 4LCA403BJ/4FAF097AT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF097AT | + | 4FAF097AT | 24Vcc |  | JB to instrument | Primary air system
|  | 13 | [5 empty] | -
4LCA403BJ | X 051 03 | 1 | 4LCA403BJ/4FAF098FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF098FT | + | 4FAF098FT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 2 | [5 empty] | -
4LCA403BJ | X 051 03 | 14 | 4LCA403BJ/4FAF099AT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF099AT | - | 4FAF099AT | 24Vcc |  | JB to instrument | Primary air system
|  | 6 | [5 empty] | + | [6 empty] | #N/A
4LCA403BJ | X 051 03 | 3 | 4LCA403BJ/4FAF100FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF100FT | + | 4FAF100FT | 24Vcc |  | JB to instrument | Primary air system
|  | 11 | [5 empty] | -
4LCA403BJ | X 31 03 | 3 | 4LCA403BJ/4FAF254FT-C-01 | U1000R2V | 3G1.5 | 12 | 4FAF254FT | 1 | 4FAF254FT | 24Vcc |  | JB to instrument | Secondary air system |  | WCC 14
|  | 7 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LCA403BJ | X 051 03 | 20 | 4LCA403BJ/4FAF254FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF254FT | 26 | 4FAF254FT | 24Vcc |  | JB to instrument | Secondary air system |  | #N/A
|  | 22 | [5 empty] | 27
4LCA403BJ | X 051 03 | 19 | 4LCA403BJ/4FAF255TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF255TT | + | 4FAF255TT | 24Vcc |  | JB to instrument | Secondary air system
|  | 24 | [5 empty] | - | [6 empty] | #N/A
4LCA403BJ | X 031 06 | 4 | 4LCA403BJ/4FGR010LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FGR010LSL | 5 | 4FGR010LSL | 24Vcc |  | JB to instrument | Fuel feeding system
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA403BJ | X 051 03 | 15 | 4LCA403BJ/4FGR057FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA057FT | - | 4FGR057FT | 24Vcc |  | JB to instrument | Primary air system
|  | 7 | [5 empty] | + | [6 empty] | #N/A
4LCA501BJ | X 051 03 | 1 | 4LCA501BJ/4EPA001TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA001TT | + | 4EPA001TT | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | -
4LCA501BJ | X 051 03 | 2 | 4LCA501BJ/4EPA002TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA002TT | + | 4EPA002TT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 7 | [5 empty] | -
4LCA501BJ | X 061 03 | 1 | 4LCA501BJ/4EPA005FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA005FCV | 6 | 4EPA005FCV | 24Vcc |  | JB to instrument | Water steam
|  | 2 | [5 empty] | 7 | [6 empty] | #N/A
4LCA501BJ | X 051 03 | 3 | 4LCA501BJ/4EPA009FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4ERF009FIT | + | 4EPA009FIT | 24Vcc |  | JB to instrument | Water steam
|  | 8 | [5 empty] | -
4LCA501BJ | X 061 03 | 3 | 4LCA501BJ/4EPA011FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA011FCV | 6 | 4EPA011FCV | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 4 | [5 empty] | 7
4LCA501BJ | X 061 03 | 5 | 4LCA501BJ/4EPA015FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA015TCV | 6 | 4EPA015FCV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
4LCA501BJ | X 051 03 | 5 | 4LCA501BJ/4FAF253PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF253PT | + | 4FAF253PT | 24Vcc |  | JB to instrument | Secondary air system
|  | 10 | [5 empty] | -
4LCA501BJ | X 061 03 | 7 | 4LCA501BJ/4FGR256HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR256HV | 6 | 4FGR256HV | 24Vcc |  | JB to instrument | Secondary air system |  | #N/A
|  | 8 | [5 empty] | 7
4LCA501BJ | X 061 03 | 9 | 4LCA501BJ/4FGR257HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR257HV | 6 | 4FGR257HV | 24Vcc |  | JB to instrument | Secondary air system
|  | 10 | [5 empty] | 7 | [6 empty] | #N/A
4LCA501BJ | X 061 03 | 11 | 4LCA501BJ/4FGR258HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR258HV | 6 | 4FGR258HV | 24Vcc |  | JB to instrument | Secondary air system
|  | 12 | [5 empty] | 7
4LCA501BJ | X 061 03 | 13 | 4LCA501BJ/4FGR260HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR260HV | 6 | 4FGR260HV | 24Vcc |  | JB to instrument | Secondary air system |  | #N/A
|  | 14 | [5 empty] | 7
4LCA501BJ | X 061 03 | 15 | 4LCA501BJ/4FTA058HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA058HV | 6 | 4FTA058HV | 24Vcc |  | JB to instrument | Fluegas recirculation system
|  | 16 | [5 empty] | 7 | [6 empty] | #N/A
4LCA501BJ | X 061 03 | 17 | 4LCA501BJ/4FTA060HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA060HV | 6 | 4FTA060HV | 24Vcc |  | JB to instrument | Flue gas
|  | 18 | [5 empty] | 7
4LCA501BJ | X 051 03 | 4 | 4LCA501BJ/4FVX003PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX003PT | + | 4FVX003PT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 9 | [5 empty] | -
4LCA501HSS |  |  | 4LCA501HSS/4LCA502HSS-C | U1000R2V | 3G1.5 | 20 |  |  | 4LCA502HSS | 24Vcc |  | JB to instrument | Ash system
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA601BJ | X 051 03 | 7 | 4LCA601BJ/4EPA003TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA003TT | + | 4EPA003TT | 24Vcc |  | JB to instrument | Water steam
|  | 12 | [5 empty] | - | [6 empty] | #N/A
4LCA601BJ | X 061 03 | 1 | 4LCA601BJ/4EPA016TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA016TCV | 6 | 4EPA016TCV | 24Vcc |  | JB to instrument | Water steam
|  | 2 | [5 empty] | 7
4LCA601BJ | X 061 03 | 3 | 4LCA601BJ/4FGR074TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR074TCV | 6 | 4FGR074TCV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 4 | [5 empty] | 7
4LCA601BJ | X 051 03 | 1 | 4LCA601BJ/4FTA028TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA028TT | 1 | 4FTA028TT | 24Vcc |  | JB to instrument | Flue gas
|  | 2 | [5 empty] | 2 | [6 empty] | #N/A
4LCA601BJ | X 051 03 | 3 | 4LCA601BJ/4FTA029TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA029TT | 1 | 4FTA029TT | 24Vcc |  | JB to instrument | Flue gas
|  | 8 | [5 empty] | 2
4LCA601BJ | X 051 03 | 6 | 4LCA601BJ/4FTA045FT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA045FT | + | 4FTA045FT | 24Vcc |  | JB to instrument | Fluegas recirculation system |  | #N/A
|  | 11 | [5 empty] | -
4LCA601BJ | X 051 03 | 5 | 4LCA601BJ/4FTA055PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA055PT | + | 4FTA055PT | 24Vcc |  | JB to instrument | Fluegas recirculation system
|  | 10 | [5 empty] | - | [6 empty] | #N/A
4LCA601BJ | X 051 03 | 4 | 4LCA601BJ/4FTA056TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA056TT | + | 4FTA056TT | 24Vcc |  | JB to instrument | Fluegas recirculation system
|  | 9 | [5 empty] | -
4LCA701BJ | X 031 03 | 1 | 4LCA701BJ/4DCA002TCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DCA002TCV | 1 | 4DCA002TCV | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 2 | [5 empty] | 2
|  | 3 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA701BJ | X 041 03 | 1 | 4LCA701BJ/4DCA002TCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM036LSH | x2 | 4DCA002TCV | 24Vcc |  | JB to instrument | Flue gas
|  | 2 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA701BJ | X 061 03 | 3 | 4LCA701BJ/4FAF094HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF094HV-6 |  | 4FAF094HV | 24Vcc |  | JB to instrument | Primary air system
|  | 4 |  |  |  |  | 4FAF094HV-7 | [7 empty] | #N/A
4LCA701BJ | X 061 03 | 5 | 4LCA701BJ/4FAF095HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF095HV-6 |  | 4FAF095HV | 24Vcc |  | JB to instrument | Primary air system
|  | 6 |  |  |  |  | 4FAF095HV-7
4LCA701BJ | X 061 03 | 1 | 4LCA701BJ/4FAF096HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF096HV-6 |  | 4FAF096HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 2 |  |  |  |  | 4FAF096HV-7
4LCA701BJ | X 051 03 | 26 | 4LCA701BJ/4FFA001LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4FFA001LT | + | 4FFA001LT | 24Vcc |  | JB to instrument | Flue gas
|  | 33 | [5 empty] | - | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 27 | 4LCA701BJ/4FFA002LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4FFA002LT | + | 4FFA002LT | 24Vcc |  | JB to instrument | Flue gas
|  | 34 | [5 empty] | -
4LCA701BJ | X 061 03 | 7 | 4LCA701BJ/4FGR063HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA063HV-6 |  | 4FGR063HV | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 8 |  |  |  |  | 4FTA063HV-7
4LCA701BJ | X 061 03 | 9 | 4LCA701BJ/4FGR064HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA064HV-6 |  | 4FGR064HV | 24Vcc |  | JB to instrument | Flue gas
|  | 10 |  |  |  |  | 4FTA064HV-7 | [7 empty] | #N/A
4LCA701BJ | X 061 03 | 11 | 4LCA701BJ/4FGR065HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA065HV-6 |  | 4FGR065HV | 24Vcc |  | JB to instrument | Flue gas
|  | 12 |  |  |  |  | 4FTA065HV-7
4LCA701BJ | X 051 03 | 8 | 4LCA701BJ/4FTA030TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA030TT | 1 | 4FTA030TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 16 | [5 empty] | 2
4LCA701BJ | X 051 03 | 11 | 4LCA701BJ/4FTA032T-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA032TT | 1 | 4FTA032T | 24Vcc |  | JB to instrument | Flue gas
|  | 19 | [5 empty] | 2 | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 14 | 4LCA701BJ/4FTA034TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA034TT | 1 | 4FTA034TT | 24Vcc |  | JB to instrument | Flue gas
|  | 22 | [5 empty] | 2
4LCA701BJ | X 051 03 | 42 | 4LCA701BJ/4FTA051PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA051PT | + | 4FTA051PT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 44 | [5 empty] | -
4LCA701BJ | X 051 03 | 43 | 4LCA701BJ/4FTA052PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA052PT | + | 4FTA052PT | 24Vcc |  | JB to instrument | Flue gas
|  | 45 | [5 empty] | - | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 37 | 4LCA701BJ/4FTA053TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA053TT | + | 4FTA053TT | 24Vcc |  | JB to instrument | Flue gas
|  | 40 | [5 empty] | -
4LCA701BJ | X 051 03 | 38 | 4LCA701BJ/4FTA054TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA054TT | + | 4FTA054TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 41 | [5 empty] | -
4LCA701BJ | X 051 03 | 36 | 4LCA701BJ/4FTA055TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA055TT | + | 4FTA055TT | 24Vcc |  | JB to instrument | Flue gas
|  | 39 | [5 empty] | - | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 3 | 4LCA701BJ/4FTA060TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA060TT | 1 | 4FTA060TT | 24Vcc |  | JB to instrument | Flue gas
|  | 6 | [5 empty] | 2
4LCA701BJ | X 051 03 | 7 | 4LCA701BJ/4FTA077T-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA077TT | 1 | 4FTA077T | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 15 | [5 empty] | 2
4LCA701BJ | X 051 03 | 10 | 4LCA701BJ/4FTA078TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA078TT | 1 | 4FTA078TT | 24Vcc |  | JB to instrument | Flue gas
|  | 18 | [5 empty] | 2 | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 13 | 4LCA701BJ/4FTA079TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA079TT | 1 | 4FTA079TT | 24Vcc |  | JB to instrument | Flue gas
|  | 21 | [5 empty] | 2
4LCA701BJ | X 051 03 | 9 | 4LCA701BJ/4FTA085TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA085TT | + | 4FTA085TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 17 | [5 empty] | -
4LCA701BJ | X 051 03 | 12 | 4LCA701BJ/4FTA086TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA086TT | + | 4FTA086TT | 24Vcc |  | JB to instrument | Flue gas
|  | 20 | [5 empty] | - | [6 empty] | #N/A
4LCA701BJ | X 051 03 | 23 | 4LCA701BJ/4FTA087T-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA087TT | 1 | 4FTA087T | 24Vcc |  | JB to instrument | Flue gas
|  | 30 | [5 empty] | 2
4LCA701BJ | X 051 03 | 28 | 4LCA701BJ/4FVX001FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX001FIT | + | 4FVX001FIT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 35 | [5 empty] | -
4LCA702BJ | X 051 03 | 2 | 4LCA702BJ/4CRF112TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF112TT | + | 4CRF112TT | 24Vcc |  | JB to instrument | Cooling water system
|  | 6 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 061 03 | 1 | 4LCA702BJ/4CRF127TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF127TCV | 6 | 4CRF127TCV | 24Vcc |  | JB to instrument | Cooling water system
|  | 2 | [5 empty] | 7
4LCA702BJ | X 051 03 | 3 | 4LCA702BJ/4CRF132TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF132TT | + | 4CRF132TT | 24Vcc |  | JB to instrument | Cooling water system |  | #N/A
|  | 7 | [5 empty] | -
4LCA702BJ | X 051 03 | 60 | 4LCA702BJ/4CTE090PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 67.1 | 4CTE090PT | + | 4CTE090PT | 24Vcc |  | JB to instrument | Cooling water
|  | 64 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 061 03 | 3 | 4LCA702BJ/4EPA017TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA017TCV | 6 | 4EPA017TCV | 24Vcc |  | JB to instrument | Water steam
|  | 4 | [5 empty] | 7
4LCA702BJ | X 061 03 | 5 | 4LCA702BJ/4FGR077TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR077TCV | 6 | 4FGR077TCV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 6 | [5 empty] | 7
4LCA702BJ | X 051 03 | 13 | 4LCA702BJ/4FTA036TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA036TT | 1 | 4FTA036TT | 24Vcc |  | JB to instrument | Flue gas
|  | 21 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 25 | 4LCA702BJ/4FTA038TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA038TT | 1 | 4FTA038TT | 24Vcc |  | JB to instrument | Flue gas
|  | 33 | [5 empty] | 2
4LCA702BJ | X 051 03 | 29 | 4LCA702BJ/4FTA040TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA040TT | 1 | 4FTA040TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 37 | [5 empty] | 2
4LCA702BJ | X 051 03 | 42 | 4LCA702BJ/4FTA042TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA042TT | 1 | 4FTA042TT | 24Vcc |  | JB to instrument | Flue gas
|  | 50 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 47 | 4LCA702BJ/4FTA044TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA044TT | + | 4FTA044TT | 24Vcc |  | JB to instrument | Flue gas
|  | 55 | [5 empty] | -
4LCA702BJ | X 051 03 | 4 | 4LCA702BJ/4FTA059PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA059PT | + | 4FTA059PT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 8 | [5 empty] | -
4LCA702BJ | X 051 03 | 9 | 4LCA702BJ/4FTA062TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA062TT | 1 | 4FTA062TT | 24Vcc |  | JB to instrument | Flue gas
|  | 17 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 10 | 4LCA702BJ/4FTA064TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA064TT | 1 | 4FTA064TT | 24Vcc |  | JB to instrument | Flue gas
|  | 18 | [5 empty] | 2
4LCA702BJ | X 051 03 | 11 | 4LCA702BJ/4FTA066TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA066TT | 1 | 4FTA066TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 19 | [5 empty] | 2
4LCA702BJ | X 051 03 | 15 | 4LCA702BJ/4FTA068TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA068TT | 1 | 4FTA068TT | 24Vcc |  | JB to instrument | Flue gas
|  | 23 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 27 | 4LCA702BJ/4FTA070TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA070TT | 1 | 4FTA070TT | 24Vcc |  | JB to instrument | Flue gas
|  | 35 | [5 empty] | 2
4LCA702BJ | X 051 03 | 32 | 4LCA702BJ/4FTA071TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA071TT | 1 | 4FTA071TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 40 | [5 empty] | 2
4LCA702BJ | X 051 03 | 45 | 4LCA702BJ/4FTA072TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA072TT | + | 4FTA072TT | 24Vcc |  | JB to instrument | Flue gas
|  | 53 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 57 | 4LCA702BJ/4FTA074TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA074TT | + | 4FTA074TT | 24Vcc |  | JB to instrument | Flue gas
|  | 61 | [5 empty] | -
4LCA702BJ | X 051 03 | 58 | 4LCA702BJ/4FTA075AT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA075AT | + | 4FTA075AT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 62 | [5 empty] | -
4LCA702BJ | X 051 03 | 12 | 4LCA702BJ/4FTA080TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA080TT | 1 | 4FTA080TT | 24Vcc |  | JB to instrument | Flue gas
|  | 20 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 16 | 4LCA702BJ/4FTA081TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA081TT | 1 | 4FTA081TT | 24Vcc |  | JB to instrument | Flue gas
|  | 24 | [5 empty] | 2
4LCA702BJ | X 051 03 | 28 | 4LCA702BJ/4FTA082TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA082TT | 1 | 4FTA082TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 36 | [5 empty] | 2
4LCA702BJ | X 051 03 | 41 | 4LCA702BJ/4FTA083TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA083TT | 1 | 4FTA083TT | 24Vcc |  | JB to instrument | Flue gas
|  | 49 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 46 | 4LCA702BJ/4FTA084TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA084TT | + | 4FTA084TT | 24Vcc |  | JB to instrument | Flue gas
|  | 54 | [5 empty] | -
4LCA702BJ | X 051 03 | 31 | 4LCA702BJ/4FTA085PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA085PT | + | 4FTA085PT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 39 | [5 empty] | -
4LCA702BJ | X 051 03 | 44 | 4LCA702BJ/4FTA086PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA086PT | + | 4FTA086PT | 24Vcc |  | JB to instrument | Flue gas
|  | 52 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 14 | 4LCA702BJ/4FTA088TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA088TT | 1 | 4FTA088TT | 24Vcc |  | JB to instrument | Flue gas
|  | 22 | [5 empty] | 2
4LCA702BJ | X 051 03 | 26 | 4LCA702BJ/4FTA089TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA089TT | 1 | 4FTA089TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 34 | [5 empty] | 2
4LCA702BJ | X 051 03 | 30 | 4LCA702BJ/4FTA090TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA090TT | 1 | 4FTA090TT | 24Vcc |  | JB to instrument | Flue gas
|  | 38 | [5 empty] | 2 | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 43 | 4LCA702BJ/4FTA091TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA091TT | 1 | 4FTA091TT | 24Vcc |  | JB to instrument | Flue gas
|  | 51 | [5 empty] | 2
4LCA702BJ | X 051 03 | 48 | 4LCA702BJ/4FTA092TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA092TT | + | 4FTA092TT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 56 | [5 empty] | -
4LCA702BJ | X 051 03 | 65 | 4LCA702BJ/4FVX001TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX001TT | + | 4FVX001TT | 24Vcc |  | JB to instrument | Water steam
|  | 68 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 1 | 4LCA702BJ/4FVX002PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX002PT | + | 4FVX002PT | 24Vcc |  | JB to instrument | Water steam
|  | 5 | [5 empty] | -
4LCA702BJ | X 051 03 | 66 | 4LCA702BJ/4FVX002TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX002TT | + | 4FVX002TT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 69 | [5 empty] | -
4LCA702BJ | X 051 03 | 67 | 4LCA702BJ/4FVX003TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX003TT | + | 4FVX003TT | 24Vcc |  | JB to instrument | Water steam
|  | 70 | [5 empty] | - | [6 empty] | #N/A
4LCA702BJ | X 051 03 | 59 | 4LCA702BJ/4FVX004TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX004TT | + | 4FVX004TT | 24Vcc |  | JB to instrument | Water steam
|  | 63 | [5 empty] | -
4LCA702BJ | X 031 03 | 1 | 4LCA702BJ/4FVX010XV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FVX010XV | 1 | 4FVX010XV | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 3 | [5 empty] | 2
|  | 5 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA702BJ | X 031 03 | 2 | 4LCA702BJ/4FVX010XV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM039LSL | 1 | 4FVX010XV | 24Vcc |  | JB to instrument | Water steam
|  | 4 | [5 empty] | 2
|  | 6 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA702BJ | X 041 03 | 1 | 4LCA702BJ/4FVX010XV-C-03 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM040LSH | x2 | 4FVX010XV | 24Vcc |  | JB to instrument | Water steam
|  | 3 | [5 empty] | x1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA702BJ | X 041 03 | 2 | 4LCA702BJ/4FVX010XV-C-04 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM064LSL | x2 | 4FVX010XV | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 4 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA801BJ | X 051 03 | 7 | 4LCA801BJ/4FSR001LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR001LT | + | 4FSR001LT | 24Vcc |  | JB to instrument | Water steam
|  | 10 | [5 empty] | -
4LCA801BJ | X 051 03 | 1 | 4LCA801BJ/4FSR001PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR001PT | + | 4FSR001PT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 4 | [5 empty] | -
4LCA801BJ | X 051 03 | 8 | 4LCA801BJ/4FSR002LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR002LT | + | 4FSR002LT | 24Vcc |  | JB to instrument | Water steam
|  | 11 | [5 empty] | - | [6 empty] | #N/A
4LCA801BJ | X 051 03 | 2 | 4LCA801BJ/4FSR002PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR002PT | + | 4FSR002PT | 24Vcc |  | JB to instrument | Water steam
|  | 5 | [5 empty] | -
4LCA801BJ | X 051 03 | 9 | 4LCA801BJ/4FSR003LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR003LT | + | 4FSR003LT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 12 | [5 empty] | -
4LCA801BJ | X 051 03 | 3 | 4LCA801BJ/4FSR003PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR003PT | + | 4FSR003PT | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | - | [6 empty] | #N/A
4LCA801BJ | X 041 03 | 1 | 4LCA801BJ/4FVA040FCV-C | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM065LSH |  | 4FVA040FCV | 24Vcc |  | JB to instrument | Water steam
5
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA801BJ | X 041 03 | 2 | 4LCA801BJ/4FVA040FCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM087LSH |  | 4FVA040FCV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA801BJ | X 041 03 | 1 | 4LCA801BJ/4JPA040FCV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4JPA040FCV | x2 | 4JPA040FCV | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 5 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA801BJ | X 041 03 | 2 | 4LCA801BJ/4JPA040FCV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4JPA040FCV | x2 | 4JPA040FCV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA802BJ | X 051 03 | 1 | 4LCA802BJ/4CRF117PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF117PT | 1 | 4CRF117PT | 24Vcc |  | JB to instrument | Cooling water system
|  | 5 | [5 empty] | 2 | [6 empty] | #N/A
4LCA802BJ | X 051 03 | 2 | 4LCA802BJ/4CRF126PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4CRF126PT | 1 | 4CRF126PT | 24Vcc |  | JB to instrument | Cooling water system
|  | 6 | [5 empty] | 2
4LCA802BJ | X 051 03 | 14 | 4LCA802BJ/4EPA004TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 20 | 4EPA004TT | + | 4EPA004TT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 22 | [5 empty] | -
4LCA802BJ | X 061 03 | 1 | 4LCA802BJ/4ERF013FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 56 | 4ERF013FCV | 6 | 4ERF013FCV | 24Vcc |  | JB to instrument | Water steam
|  | 2 | [5 empty] | 7 | [6 empty] | #N/A
4LCA802BJ | X 061 03 | 3 | 4LCA802BJ/4ERF019FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 56 | 4ERF019FCV | 6 | 4ERF019FCV | 24Vcc |  | JB to instrument | Water steam
|  | 4 | [5 empty] | 7
4LCA802BJ | X 051 03 | 3 | 4LCA802BJ/4FAF080PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF080PT | + | 4FAF080PT | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 7 | [5 empty] | -
4LCA802BJ | X 051 03 | 4 | 4LCA802BJ/4FAF081TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FAF081TT | + | 4FAF081TT | 24Vcc |  | JB to instrument | Primary air system
|  | 8 | [5 empty] | - | [6 empty] | #N/A
4LCA802BJ | X 061 03 | 9 | 4LCA802BJ/4FGR059HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR059HV | 6 | 4FGR059HV | 24Vcc |  | JB to instrument | Primary air system
|  | 10 | [5 empty] | 7
4LCA802BJ | X 061 03 | 13 | 4LCA802BJ/4FGR060HV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR060HV | 6 | 4FGR060HV | 24Vcc |  | JB to instrument | Primary air system |  | #N/A
|  | 14 | [5 empty] | 7
4LCA802BJ | X 061 03 | 7 | 4LCA802BJ/4FGR076TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FGR076TCV | 6 | 4FGR076TCV | 24Vcc |  | JB to instrument | Primary air system
|  | 8 | [5 empty] | 7 | [6 empty] | #N/A
4LCA802BJ | X 031 03 | 1 | 4LCA802BJ/4FSE002XV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FSE002XV | 1 | 4FSE002XV | 24Vcc |  | JB to instrument | Water steam
|  | 5 | [5 empty] | 2
|  | 9 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA802BJ | X 031 03 | 2 | 4LCA802BJ/4FSE002XV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4DEM088LSL | 1 | 4FSE002XV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
|  | 10 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA802BJ | X 041 03 | 1 | 4LCA802BJ/4FSE002XV-C-03 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA122LCV | x2 | 4FSE002XV | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 3 | [5 empty] | x1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA802BJ | X 041 03 | 2 | 4LCA802BJ/4FSE002XV-C-04 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 0 | x2 | 4FSE002XV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA802BJ | X 061 03 | 5 | 4LCA802BJ/4FSE003FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSE003FCV | 6 | 4FSE003FCV | 24Vcc |  | JB to instrument | Water steam
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
4LCA802BJ | X 051 03 | 15 | 4LCA802BJ/4FSR001TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR001TT | + | 4FSR001TT | 24Vcc |  | JB to instrument | Water steam
|  | 23 | [5 empty] | -
4LCA802BJ | X 051 03 | 16 | 4LCA802BJ/4FSR002TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR002TT | + | 4FSR002TT | 24Vcc |  | JB to instrument | Water steam |  | #N/A
|  | 24 | [5 empty] | -
4LCA802BJ | X 051 03 | 25 | 4LCA802BJ/4FSR003TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR003TT | + | 4FSR003TT | 24Vcc |  | JB to instrument | Water steam
|  | 28 | [5 empty] | - | [6 empty] | #N/A
4LCA802BJ | X 051 03 | 26 | 4LCA802BJ/4FSR004TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSR004TT | + | 4FSR004TT | 24Vcc |  | JB to instrument | Water steam
|  | 29 | [5 empty] | -
4LCA802BJ | X 051 03 | 9 | 4LCA802BJ/4FTA061PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA061PT | + | 4FTA061PT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 17 | [5 empty] | -
4LCA802BJ | X 051 03 | 10 | 4LCA802BJ/4FTA063PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA063PT | + | 4FTA063PT | 24Vcc |  | JB to instrument | Flue gas
|  | 18 | [5 empty] | - | [6 empty] | #N/A
4LCA802BJ | X 051 03 | 11 | 4LCA802BJ/4FTA065PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA065PT | + | 4FTA065PT | 24Vcc |  | JB to instrument | Flue gas
|  | 19 | [5 empty] | -
4LCA802BJ | X 051 03 | 12 | 4LCA802BJ/4FTA067PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA067PT | + | 4FTA067PT | 24Vcc |  | JB to instrument | Flue gas |  | #N/A
|  | 20 | [5 empty] | -
4LCA802BJ | X 051 03 | 13 | 4LCA802BJ/4FTA076PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FTA076PT | + | 4FTA076PT | 24Vcc |  | JB to instrument | Flue gas
|  | 21 | [5 empty] | - | [6 empty] | #N/A
4LCA802BJ | X 061 03 | 11 | 4LCA802BJ/4FVX015XV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX015XV | 6 | 4FVX015XV | 24Vcc |  | JB to instrument | Water steam
|  | 12 | [5 empty] | 7
4LCA802BJ | X 051 03 | 27 | 4LCA802BJ/4SEO003FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 55 | 4SEO003FIT | + | 4SEO003FIT | 24Vcc |  | JB to instrument | Drain&Vent |  | #N/A
|  | 30 | [5 empty] | -
4LCA901BJ | X 051 03 | 22 | 4LCA901BJ/4EBA001LT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA001LT | + | 4EBA001LT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 30 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 21 | 4LCA901BJ/4EBA001TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA001TT | + | 4EBA001TT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 29 | [5 empty] | -
4LCA901BJ | X 031 03 | 3 | 4LCA901BJ/4EBA002LSH-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA002LSH | 1 | 4EBA002LSH | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 11 | [5 empty] | 2
|  | 19 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA901BJ | X 031 03 | 4 | 4LCA901BJ/4EBA002LSL-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EBA002LSL | 1 | 4EBA002LSL | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 12 | [5 empty] | 2
|  | 20 | [5 empty] | 3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA901BJ | X 061 03 | 5 | 4LCA901BJ/4EBA011TCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA011TCV | 6 | 4EBA011TCV | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 23 | 4LCA901BJ/4EBA021PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA021PT | + | 4EBA021PT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 31 | [5 empty] | -
4LCA901BJ | X 051 03 | 24 | 4LCA901BJ/4EBA022PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA022PT | + | 4EBA022PT | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 32 | [5 empty] | -
4LCA901BJ | X 051 03 | 33 | 4LCA901BJ/4EBA024PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA024PT | 1 | 4EBA024PT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 41 | [5 empty] | 2 | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 54 | 4LCA901BJ/4EBA028FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA028FIT | + | 4EBA028FIT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 60 | [5 empty] | -
4LCA901BJ | X 061 03 | 7 | 4LCA901BJ/4EBA032LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA032LCV | 6 | 4EBA032LCV | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 8 | [5 empty] | 7
4LCA901BJ | X 061 03 | 9 | 4LCA901BJ/4EBA035LCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA035LCV | 6 | 4EBA035LCV | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 10 | [5 empty] | 7 | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 34 | 4LCA901BJ/4EBA041PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA041PT | 1 | 4EBA041PT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 42 | [5 empty] | 2
4LCA901BJ | X 051 03 | 35 | 4LCA901BJ/4EBA042PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA042PT | + | 4EBA042PT | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 43 | [5 empty] | -
4LCA901BJ | X 051 03 | 36 | 4LCA901BJ/4EBA044PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA044PT | + | 4EBA044PT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 44 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 38 | 4LCA901BJ/4EBA053TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA053TT | + | 4EBA053TT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 46 | [5 empty] | -
4LCA901BJ | X 051 03 | 37 | 4LCA901BJ/4EBA065FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA065FIT | + | 4EBA065FIT | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 45 | [5 empty] | -
4LCA901BJ | X 051 03 | 61 | 4LCA901BJ/4EBA066FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA066FIT | + | 4EBA066FIT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 63 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 8 | 4LCA901BJ/4EBA130FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA130FIT | + | 4EBA130FIT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 16 | [5 empty] | -
4LCA901BJ | X 051 03 | 17 | 4LCA901BJ/4EBA131TI-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA131TI | + | 4EBA131TI | 24Vcc |  | JB to instrument ABR | Thermal water treatment |  | #N/A
|  | 25 | [5 empty] | -
4LCA901BJ | X 051 03 | 18 | 4LCA901BJ/4EBA132PI-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA132PI | + | 4EBA132PI | 24Vcc |  | JB to instrument ABR | Thermal water treatment
|  | 26 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 19 | 4LCA901BJ/4EBA133PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA133PT | + | 4EBA133PT | 24Vcc |  | JB to instrument ABR | Thermal water treatment
|  | 27 | [5 empty] | -
4LCA901BJ | X 051 03 | 50 | 4LCA901BJ/4EBA206PIC-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4EBA206PIC | + | 4EBA206PIC | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 56 | [5 empty] | -
4LCA901BJ | X 031 03 | 1 | 4LCA901BJ/4FSE386XV-C-01 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4FSE386XV | 1 | 4FSE386XV | 24Vcc |  | JB to instrument ABR | HP steam
|  | 9 | [5 empty] | 2 | [6 empty] | #N/A
|  | 17 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE
4LCA901BJ | X 031 03 | 2 | 4LCA901BJ/4FSE386XV-C-02 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 0 | 1 | 4FSE386XV | 24Vcc |  | JB to instrument ABR | HP steam |  | #N/A
|  | 10 | [5 empty] | 2
|  | 18 | [5 empty] | 3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LCA901BJ | X 041 03 | 1 | 4LCA901BJ/4FSE386XV-C-03 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EPA103PT | x2 | 4FSE386XV | 24Vcc |  | JB to instrument ABR | HP steam
|  | 5 | [5 empty] | x1
#N/A
| PE | PE |  |  |  |  | PE | PE
4LCA901BJ | X 041 03 | 2 | 4LCA901BJ/4FSE386XV-C-04 | BIRTFLEX 511-PVC-PUR-JB | 4G0.75 | 12 | 4EPA111ZSH | x2 | 4FSE386XV | 24Vcc |  | JB to instrument ABR | HP steam
|  | 6 | [5 empty] | x1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LCA901BJ | X 061 03 | 1 | 4LCA901BJ/4FSE387FCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FSE387FCV | 6 | 4FSE387FCV | 24Vcc |  | JB to instrument ABR | HP steam |  | #N/A
|  | 2 | [5 empty] | 7
4LCA901BJ | X 051 03 | 1 | 4LCA901BJ/4FVX300PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX300PT | 1 | 4FVX300PT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 9 | [5 empty] | 2 | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 4 | 4LCA901BJ/4FVX303TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX303TT | + | 4FVX303TT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 12 | [5 empty] | -
4LCA901BJ | X 051 03 | 5 | 4LCA901BJ/4FVX304PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX304PT | + | 4FVX304PT | 24Vcc |  | JB to instrument ABR | HP steam |  | #N/A
|  | 13 | [5 empty] | -
4LCA901BJ | X 051 03 | 6 | 4LCA901BJ/4FVX306TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX306TT | + | 4FVX306TT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 14 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 7 | 4LCA901BJ/4FVX307PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX307PT | + | 4FVX307PT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 15 | [5 empty] | -
4LCA901BJ | X 051 03 | 3 | 4LCA901BJ/4FVX315FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX315FIT | + | 4FVX315FIT | 24Vcc |  | JB to instrument ABR | HP steam |  | #N/A
|  | 11 | [5 empty] | -
4LCA901BJ | X 051 03 | 51 | 4LCA901BJ/4FVX316FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX316FIT | + | 4FVX316FIT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 57 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 2 | 4LCA901BJ/4FVX330FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX330FIT | 1 | 4FVX330FIT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 10 | [5 empty] | 2
4LCA901BJ | X 051 03 | 39 | 4LCA901BJ/4FVX401PICAH-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX401PICAH | + | 4FVX401PICAH | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 47 | [5 empty] | -
4LCA901BJ | X 051 03 | 40 | 4LCA901BJ/4FVX401TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX401TT | + | 4FVX401TT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 48 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 061 03 | 3 | 4LCA901BJ/4FVX403PCV-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX403PCV | 6 | 4FVX403PCV | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 4 | [5 empty] | 7
4LCA901BJ | X 051 03 | 52 | 4LCA901BJ/4FVX413PT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX413PT | + | 4FVX413PT | 24Vcc |  | JB to instrument ABR | Condensate system |  | #N/A
|  | 58 | [5 empty] | -
4LCA901BJ | X 051 03 | 53 | 4LCA901BJ/4FVX413TT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX413TT | + | 4FVX413TT | 24Vcc |  | JB to instrument ABR | Condensate system
|  | 59 | [5 empty] | - | [6 empty] | #N/A
4LCA901BJ | X 051 03 | 49 | 4LCA901BJ/4FVX415FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 12 | 4FVX415FIT | + | 4FVX415FIT | 24Vcc |  | JB to instrument ABR | HP steam
|  | 55 | [5 empty] | -
4LCA901BJ | X 051 03 | 20 | 4LCA901BJ/4SDX101FIC-M-01 | 01IP09EGSF BU | 1x2x0.88 | 100 | 4SDX101FIC | + | 4SDX101FIC | 24Vcc |  | JB to instrument ABR | Thermal water treatment |  | #N/A
|  | 28 | [5 empty] | -
4LCA901BJ | X 051 03 | 62 | 4LCA901BJ/4SEB009FIT-M-01 | 01IP09EGSF BU | 1x2x0.88 | 58 | 4SEB009FIT | + | 4SEB009FIT | 24Vcc |  | JB to instrument ABR | Wet cleaning system
|  | 64 | [5 empty] | - | [6 empty] | #N/A
4LGA004DJ | X? | A | 4LGA004DJ/4KLD006CQ-C-01 | U1000R2V | 5G1.5 | 25 | X 211 03 | 1 | 4KLD006CQ | 48Vca |  | HV room
|  | A | [5 empty] | 2
|  | A |  |  |  |  | X 251 03 | 8 | [6 empty] | #N/A
|  | A | [5 empty] | 9
| PE | PE |  |  |  |  | PE | PE
4LGA005DJ | X? | A | 4LGA005DJ/4KLD006CQ-C-01 | U1000R2V | 5G1.5 | 25 | X 211 03 | 3 | 4KLD006CQ | 48Vca |  | HV room |  |  | WCC 14
|  | A | [5 empty] | 4
|  | A |  |  |  |  | X 251 03 | 11
|  | A | [5 empty] | 12 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LGA006DJ | X? | A | 4LGA006DJ/4KLD006CQ-C-01 | U1000R2V | 5G1.5 | 25 | X 211 03 | 5 | 4KLD006CQ | 48Vca |  | HV room
|  | A | [5 empty] | 6 | [6 empty] | #N/A
|  | A |  |  |  |  | X 251 03 | 15
|  | A | [5 empty] | 16
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LHA001AR | QB 042 05 | 2 | 4LHA001AR/4EPA055VAR-B-01 | U1000R2V | 1x185 | 35 | IG 031 04 | 1 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L1 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 042 05 | 4 | 4LHA001AR/4EPA055VAR-B-02 | U1000R2V | 1x185 | 35 | IG 031 04 | 3 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L2 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 042 05 | 6 | 4LHA001AR/4EPA055VAR-B-03 | U1000R2V | 1x185 | 35 | IG 031 04 | 5 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L3 | 1st floor | Thermal water treatment | PRIO | WCC 26
4LHA001AR | PE | PE | 4LHA001AR/4EPA055VAR-B-04 | U1000R2V | 1x185 | 35 | PE | PE | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 PE | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 042 05 | 2 | 4LHA001AR/4EPA055VAR-B-05 | U1000R2V | 1x185 | 35 | IG 031 04 | 1 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L1 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 042 05 | 4 | 4LHA001AR/4EPA055VAR-B-06 | U1000R2V | 1x185 | 35 | IG 031 04 | 3 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L2 | 1st floor | Thermal water treatment | PRIO | WCC 26
4LHA001AR | QB 042 05 | 6 | 4LHA001AR/4EPA055VAR-B-07 | U1000R2V | 1x185 | 35 | IG 031 04 | 5 | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 L3 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4EPA055VAR-B-08 | U1000R2V | 1x185 | 35 | PE | PE | 4EPA055VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 1 PE | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 043 05 | 2 | 4LHA001AR/4EPA075VAR-B-01 | U1000R2V | 1x185 | 35 | IG 031 04 | 1 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L1 | 1st floor | Thermal water treatment | PRIO | WCC 26
4LHA001AR | QB 043 05 | 4 | 4LHA001AR/4EPA075VAR-B-02 | U1000R2V | 1x185 | 35 | IG 031 04 | 3 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L2 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 043 05 | 6 | 4LHA001AR/4EPA075VAR-B-03 | U1000R2V | 1x185 | 35 | IG 031 04 | 5 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L3 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4EPA075VAR-B-04 | U1000R2V | 1x185 | 35 | PE | PE | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 PE | 1st floor | Thermal water treatment | PRIO | WCC 26
4LHA001AR | QB 043 05 | 2 | 4LHA001AR/4EPA075VAR-B-05 | U1000R2V | 1x185 | 35 | IG 031 04 | 1 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L1 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 043 05 | 4 | 4LHA001AR/4EPA075VAR-B-06 | U1000R2V | 1x185 | 35 | IG 031 04 | 3 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L2 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 043 05 | 6 | 4LHA001AR/4EPA075VAR-B-07 | U1000R2V | 1x185 | 35 | IG 031 04 | 5 | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 L3 | 1st floor | Thermal water treatment | PRIO | WCC 26
4LHA001AR | PE | PE | 4LHA001AR/4EPA075VAR-B-08 | U1000R2V | 1x185 | 35 | PE | PE | 4EPA075VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD POMPE EAU ALIMENTAIRE 2 PE | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 2 | 4LHA001AR/4FTA040AR-B-01 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L1 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 4 | 4LHA001AR/4FTA040AR-B-02 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L2 | 1st floor | Thermal water treatment | PRIO | WCC 30
4LHA001AR | QB 038 05 | 6 | 4LHA001AR/4FTA040AR-B-03 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L3 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4FTA040AR-B-04 | U1000R2V | 1x185 | 12 | PE | PE | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE PE | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 2 | 4LHA001AR/4FTA040AR-B-05 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L1 | 1st floor | Thermal water treatment | PRIO | WCC 30
4LHA001AR | QB 038 05 | 4 | 4LHA001AR/4FTA040AR-B-06 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L2 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 6 | 4LHA001AR/4FTA040AR-B-07 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L3 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 2 | 4LHA001AR/4FTA040AR-B-08 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L1 | 1st floor | Thermal water treatment | PRIO | WCC 30
4LHA001AR | QB 038 05 | 4 | 4LHA001AR/4FTA040AR-B-09 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L2 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 038 05 | 6 | 4LHA001AR/4FTA040AR-B-10 | U1000R2V | 1x240 | 12 |  |  | 4FTA040AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE TIRAGE L3 | 1st floor | Thermal water treatment | PRIO
4LHA001AR | QB 041 05 | 2 | 4LHA001AR/4FTA049VAR-B-01 | U1000R2V | 1x120 | 35 | IG 031 04 | 1 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L1 | 1st floor | Secondary air system | PRIO | WCC 22
4LHA001AR | QB 041 05 | 4 | 4LHA001AR/4FTA049VAR-B-02 | U1000R2V | 1x120 | 35 | IG 031 04 | 3 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L2 | 1st floor | Secondary air system | PRIO
4LHA001AR | QB 041 05 | 6 | 4LHA001AR/4FTA049VAR-B-03 | U1000R2V | 1x120 | 35 | IG 031 04 | 5 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L3 | 1st floor | Secondary air system | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4FTA049VAR-B-04 | U1000R2V | 1x120 | 35 | PE | PE | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES PE | 1st floor | Secondary air system | PRIO | WCC 22
4LHA001AR | QB 041 05 | 2 | 4LHA001AR/4FTA049VAR-B-05 | U1000R2V | 1x120 | 35 | IG 031 04 | 1 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L1 | 1st floor | Secondary air system | PRIO
4LHA001AR | QB 041 05 | 4 | 4LHA001AR/4FTA049VAR-B-06 | U1000R2V | 1x120 | 35 | IG 031 04 | 3 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L2 | 1st floor | Secondary air system | PRIO
4LHA001AR | QB 041 05 | 6 | 4LHA001AR/4FTA049VAR-B-07 | U1000R2V | 1x120 | 35 | IG 031 04 | 5 | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES L3 | 1st floor | Secondary air system | PRIO | WCC 22
4LHA001AR | PE | PE | 4LHA001AR/4FTA049VAR-B-08 | U1000R2V | 1x120 | 35 | PE | PE | 4FTA049VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR DE RECIRCULATION DES FUMÉES PE | 1st floor | Secondary air system | PRIO
4LHA001AR | X 037 04 | 4 | 4LHA001AR/4LKA001AR-C-01 | U1000R2V | 5G1.5 | 50 | X 031 06 | 3 | 4LKA001AR | 24Vcc |  | 1st floor | Secondary air system
| X 037 07 | 1 | [5 empty] | 6 | [6 empty] | #N/A
|  | 2 | [5 empty] | 5
|  | 3 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LHA001AR | QB 040 05 | 2 | 4LHA001AR/4LKF001AR-B-01 | U1000R2V | 1x300 | 35 | IG 031 05 |  | 4LKF001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (SECOURUE) L1 | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 040 05 | 4 | 4LHA001AR/4LKF001AR-B-02 | U1000R2V | 1x300 | 35 | IG 031 05 | 4 | 4LKF001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (SECOURUE) L2 | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 040 05 | 6 | 4LHA001AR/4LKF001AR-B-03 | U1000R2V | 1x300 | 35 | IG 031 05 | 6 | 4LKF001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (SECOURUE) L3 | 1st to 2nd floor |  | PRIO | WCC 30
4LHA001AR | PE | PE | 4LHA001AR/4LKF001AR-B-04 | U1000R2V | 1x150 | 35 | PE | 1 | 4LKF001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (SECOURUE) PE | 1st to 2nd floor |  | PRIO
4LHA001AR | X 048 13 | 2 | 4LHA001AR/4LKF001AR-S-01 |  |  | 35 | X 038 10 | 1 | 4LKF001AR |  |  | 1st to 2nd floor
4LHA001AR | X 048 13 | 1 | 4LHA001AR/4LKF001AR-S-02 |  |  | 35 |  |  | 4LKF001AR |  |  | 1st to 2nd floor |  |  | #N/A
4LHA001AR | QB 046 05 | 2 | 4LHA001AR/4LKM001TR-B-01 | U1000R2V | 1x300 | 35 |  |  | 4LKM001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DISTRIBUTION UTILITES L1 | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 046 05 | 4 | 4LHA001AR/4LKM001TR-B-02 | U1000R2V | 1x300 | 35 |  |  | 4LKM001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DISTRIBUTION UTILITES L2 | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 046 05 | 6 | 4LHA001AR/4LKM001TR-B-03 | U1000R2V | 1x300 | 35 |  |  | 4LKM001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DISTRIBUTION UTILITES L3 | 1st to 2nd floor |  | PRIO | WCC 30
4LHA001AR | PE | PE | 4LHA001AR/4LKM001TR-B-04 | U1000R2V | 1x150 | 35 |  |  | 4LKM001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DISTRIBUTION UTILITES PE | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 039 05 | 2 | 4LHA001AR/4LKN001TR-B-01 | U1000R2V | 1x240 | 35 |  |  | 4LKN001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DE DISTRIBUTION LOCAUX ADMINISTRATIFS ET DIVERS BATIMENT L1 | 1st to 3rd floor |  | PRIO
4LHA001AR | QB 039 05 | 4 | 4LHA001AR/4LKN001TR-B-02 | U1000R2V | 1x240 | 35 |  |  | 4LKN001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DE DISTRIBUTION LOCAUX ADMINISTRATIFS ET DIVERS BATIMENT L2 | 1st to 3rd floor |  | PRIO | WCC 30
4LHA001AR | QB 039 05 | 6 | 4LHA001AR/4LKN001TR-B-03 | U1000R2V | 1x240 | 35 |  |  | 4LKN001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DE DISTRIBUTION LOCAUX ADMINISTRATIFS ET DIVERS BATIMENT L3 | 1st to 3rd floor |  | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4LKN001TR-B-04 | U1000R2V | 1x120 | 35 |  |  | 4LKN001TR | 400Vca | ALIMENTATION PRINCIPALE TABLEAU DE DISTRIBUTION LOCAUX ADMINISTRATIFS ET DIVERS BATIMENT PE | 1st to 3rd floor |  | PRIO
4LHA001AR | QB 047 05 | 2 | 4LHA001AR/4LMA001TR-B-01 | U1000R2V | 1x95 | 35 |  |  | 4LMA001TR | 400Vca | ALIMENTATION PRINCIPALE ALIMENTATION UPS L1 | 1st to 2nd floor |  | PRIO | WCC 18
4LHA001AR | QB 047 05 | 4 | 4LHA001AR/4LMA001TR-B-02 | U1000R2V | 1x95 | 35 |  |  | 4LMA001TR | 400Vca | ALIMENTATION PRINCIPALE ALIMENTATION UPS L2 | 1st to 2nd floor |  | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4LMA001TR-B-03 | U1000R2V | 1x95 | 35 |  |  | 4LMA001TR | 400Vca | ALIMENTATION PRINCIPALE ALIMENTATION UPS PE | 1st to 2nd floor |  | PRIO
4LHA001AR | QB 044 05 | 2 | 4LHA001AR/4SAR001AR-B-01 | U1000R2V | 1x95 | 40 |  |  | 4SAR001AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 1 L1 | 1st floor to process area | Pneumatic system | PRIO | WCC 18
4LHA001AR | QB 044 05 | 4 | 4LHA001AR/4SAR001AR-B-02 | U1000R2V | 1x95 | 40 |  |  | 4SAR001AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 1 L2 | 1st floor to process area | Pneumatic system | PRIO
4LHA001AR | QB 044 05 | 6 | 4LHA001AR/4SAR001AR-B-03 | U1000R2V | 1x95 | 40 |  |  | 4SAR001AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 1 L3 | 1st floor to process area | Pneumatic system | PRIO
4LHA001AR | PE | PE | 4LHA001AR/4SAR001AR-B-04 | U1000R2V | 1x50 | 40 |  |  | 4SAR001AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 1 PE | 1st floor to process area | Pneumatic system | PRIO | WCC 18
4LHA001AR | QB 045 05 | 2 | 4LHA001AR/4SAR002AR-B-01 | U1000R2V | 1x95 | 40 |  |  | 4SAR002AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 2 L1 | 1st floor to process area | Pneumatic system | PRIO
4LHA001AR | QB 045 05 | 4 | 4LHA001AR/4SAR002AR-B-02 | U1000R2V | 1x95 | 40 |  |  | 4SAR002AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 2 L2 | 1st floor to process area | Pneumatic system | PRIO
4LHA001AR | QB 045 05 | 6 | 4LHA001AR/4SAR002AR-B-03 | U1000R2V | 1x95 | 40 |  |  | 4SAR002AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 2 L3 | 1st floor to process area | Pneumatic system | PRIO | WCC 18
4LHA001AR | PE | PE | 4LHA001AR/4SAR002AR-B-04 | U1000R2V | 1x50 | 40 |  |  | 4SAR002AR | 400Vca | ALIMENTATION PRINCIPALE COMPRESSEUR 2 PE | 1st floor to process area | Pneumatic system | PRIO
4LHA001AR | IG 031 02 | 82 | 4LHA001AR/54655_1 | 08IP09EISF BU | 8x2x0.88 | 35 | KF 033 06 | N | 54655_1 | 24Vcc |  |  | Thermal water treatment
|  | 251 | [5 empty] | R | [6 empty] | #N/A
|  | 12 | [5 empty] | N
|  | A1 | [5 empty] | R
|  | 14 | [5 empty] | N | [6 empty] | #N/A
|  | C2 | [5 empty] | R
|  | B2 | [5 empty] | N
|  | 11 | [5 empty] | R | [6 empty] | #N/A
| IG 032 02 | 82 | [5 empty] | N
|  | 251 | [5 empty] | R
|  | 12 | [5 empty] | N | [6 empty] | #N/A
|  | A1 | [5 empty] | R
|  | 14 | [5 empty] | N
|  | C2 | [5 empty] | R | [6 empty] | #N/A
|  | B2 | [5 empty] | N
|  | 11 | [5 empty] | R
4LHA001AR | P 048 13 | + | 4LHA001AR/P 048 13 | PROFIBUS CABLE |  | 35 | X 048 13 | 1 | P 048 13 | 24Vcc |  |  | Thermal water treatment |  | #N/A
|  | 4 | [5 empty] | 2
| PE | PE
4LKA001AR | QA 072 04 | 2/T1 | 4LKA001AR/4EPA001CQ-B-01 | U1000R2V | 4G50 | 65 |  |  | 4EPA001CQ | 400Vca | ALIMENTATION PRINCIPALE POMPE HYDRAULIQUE PRINCIPALE 1 | 1st floor to process area | Hydraulic cylinder | PRIO | #DIV/0!
4/T2
6/T3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 073 10 | 1 | 4LKA001AR/4EPA001CQ-C-01 | U1000R2V | 5G1.5 | 65 | X? | ? | 4EPA001CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder
|  | 2 | [5 empty] | ?
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 075 04 | 4 | 4LKA001AR/4EPA001CQ-C-02 | U1000R2V | 3G1.5 | 65 | X? | ? | 4EPA001CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder |  | #N/A
|  | 5 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | QA 076 04 | 2/T1 | 4LKA001AR/4EPA002CQ-B-01 | U1000R2V | 4G50 | 65 |  |  | 4EPA002CQ | 400Vca | ALIMENTATION PRINCIPALE POMPE HYDRAULIQUE PRINCIPALE 2 | 1st floor to process area | Hydraulic cylinder | PRIO | #DIV/0!
4/T2
6/T3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 077 10 | 1 | 4LKA001AR/4EPA002CQ-C-01 | U1000R2V | 5G1.5 | 65 | X? | ? | 4EPA002CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder
|  | 2 | [5 empty] | ?
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 079 04 | 7 | 4LKA001AR/4EPA002CQ-C-02 | U1000R2V | 3G1.5 | 65 | X? | ? | 4EPA002CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder |  | #N/A
|  | 8 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | QA 080 04 | 2/T1 | 4LKA001AR/4EPA003CQ-B-01 | U1000R2V | 4G50 | 65 |  |  | 4EPA003CQ | 400Vca | ALIMENTATION PRINCIPALE POMPE HYDRAULIQUE PRINCIPALE 3 | 1st floor to process area | Hydraulic cylinder | PRIO | #DIV/0!
4/T2
6/T3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 081 10 | 1 | 4LKA001AR/4EPA003CQ-C-01 | U1000R2V | 5G1.5 | 65 | X? | ? | 4EPA003CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder
|  | 2 | [5 empty] | ?
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 079 04 | 15 | 4LKA001AR/4EPA003CQ-C-02 | U1000R2V | 3G1.5 | 65 | X? | ? | 4EPA003CQ | 24Vcc |  | 1st floor to process area | Hydraulic cylinder |  | #N/A
|  | 16 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | QB 043 05 | 2 | 4LKA001AR/4FAF065VAR-B-01 | U1000R2V | 1x120 | 33 | IG 031 04 | 1 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L1 | 1st floor | Primary air system | PRIO | WCC 22
4LKA001AR | QB 043 05 | 4 | 4LKA001AR/4FAF065VAR-B-02 | U1000R2V | 1x120 | 33 | IG 031 05 | 3 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L2 | 1st floor | Primary air system | PRIO
4LKA001AR | QB 043 05 | 6 | 4LKA001AR/4FAF065VAR-B-03 | U1000R2V | 1x120 | 33 | IG 031 06 | 5 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L3 | 1st floor | Primary air system | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4FAF065VAR-B-04 | U1000R2V | 1x120 | 33 | PE | PE | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE PE | 1st floor | Primary air system | PRIO | WCC 22
4LKA001AR | QB 043 05 | 2 | 4LKA001AR/4FAF065VAR-B-05 | U1000R2V | 1x120 | 33 | IG 031 08 | 1 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L1 | 1st floor | Primary air system | PRIO
4LKA001AR | QB 043 05 | 4 | 4LKA001AR/4FAF065VAR-B-06 | U1000R2V | 1x120 | 33 | IG 031 09 | 3 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L2 | 1st floor | Primary air system | PRIO
4LKA001AR | QB 043 05 | 6 | 4LKA001AR/4FAF065VAR-B-07 | U1000R2V | 1x120 | 33 | IG 031 10 | 5 | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE L3 | 1st floor | Primary air system | PRIO | WCC 22
4LKA001AR | PE | PE | 4LKA001AR/4FAF065VAR-B-08 | U1000R2V | 1x120 | 33 | PE | PE | 4FAF065VAR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE VFD VENTILATEUR D'AIR PRIMAIRE PE | 1st floor | Primary air system | PRIO
4LKA001AR | X 057 05 | 6 | 4LKA001AR/4FGO015CA-C-01 | U1000R2V | 5G1.5 | 30 | X? | ? | 4FGO015CA | 24Vcc |  |  | Burners and control valves
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
|  | 16 | [5 empty] | ?
|  | 17 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 065 05 | 6 | 4LKA001AR/4FGO016CA-C-01 | U1000R2V | 5G1.5 | 32 | X? | ? | 4FGO016CA | 24Vcc |  |  | Burners and control valves
|  | 7 | [5 empty] | ?
|  | 17 | [5 empty] | ? | [6 empty] | #N/A
|  | 16 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 059 06 | 2 | 4LKA001AR/4FGO101CR-C-01 | U1000R2V | 5G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves |  | #N/A
|  | 3 | [5 empty] | ?
|  | 6 | [5 empty] | ?
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 057 05 | 14 | 4LKA001AR/4FGO101CR-C-02 | U1000R2V | 3G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves
|  | 15 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 060 04 | 1 | 4LKA001AR/4FGO101CR-C-03 | U1000R2V | 5G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves
|  | 4 | [5 empty] | ? | [6 empty] | #N/A
|  | 6 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 067 06 | 2 | 4LKA001AR/4FGO101CR-C-04 | U1000R2V | 5G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves
|  | 3 | [5 empty] | ?
|  | 6 | [5 empty] | ? | [6 empty] | #N/A
|  | 7 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 065 05 | 14 | 4LKA001AR/4FGO101CR-C-05 | U1000R2V | 3G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves |  | #N/A
|  | 15 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 068 04 | 1 | 4LKA001AR/4FGO101CR-C-06 | U1000R2V | 5G1.5 | 35 | X? | ? | 4FGO101CR | 24Vcc |  |  | Burners and control valves |  | #N/A
|  | 4 | [5 empty] | ?
|  | 6 | [5 empty] | ?
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 049 05 | 12 | 4LKA001AR/4FGR247CA-C-01 | U1000R2V | 5G1.5 | 35 | X? | ? | 4FGR247CA | 24Vcc |  | 1st floor to process area | Primary air system
|  | 13 | [5 empty] | ? | [6 empty] | #N/A
|  | 17 | [5 empty] | ?
|  | 16 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | QB 054 05 | 2 | 4LKA001AR/4KCL999CQ-B-01 | U1000R2V | 4G70 | 35 | TA 201 05 | L1 | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR DU BRÛLEUR 1 | 1st floor | Secondary air system | PRIO
|  | 4 | [5 empty] | L2
|  | 6 | [5 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | QB 062 05 | 2 | 4LKA001AR/4KCL999CQ-B-02 | U1000R2V | 4G70 | 35 | TA 202 05 | L1 | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR DU BRÛLEUR 2 | 1st floor | Secondary air system | PRIO
|  | 4 | [5 empty] | L2 | [6 empty] | #N/A
|  | 6 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | QB 046 05 | 2 | 4LKA001AR/4KCL999CQ-B-03 | U1000R2V | 1x120 | 35 | TA 203 02 | L1 | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR SECONDAIRE L1 | 1st floor | Secondary air system | PRIO | WCC 22
4LKA001AR | QB 046 05 | 4 | 4LKA001AR/4KCL999CQ-B-04 | U1000R2V | 1x120 | 35 | TA 203 02 | L2 | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR SECONDAIRE L2 | 1st floor | Secondary air system | PRIO
4LKA001AR | QB 046 05 | 6 | 4LKA001AR/4KCL999CQ-B-05 | U1000R2V | 1x120 | 35 | TA 203 02 | L3 | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR SECONDAIRE L3 | 1st floor | Secondary air system | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4KCL999CQ-B-06 | U1000R2V | 1x120 | 35 | PE | PE | 4KCL999CQ | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE CHASSIS VARIATEURS VENTILATEUR D'AIR SECONDAIRE PE | 1st floor | Secondary air system | PRIO | WCC 22
4LKA001AR | X 054 15 | 3 | 4LKA001AR/4KCL999CQ--01 | U1000R2V | 5G1.5 | 20 | X 054 07 | 1 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system
|  | 7 | [5 empty] | 5
|  | 8 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 055 07 | 1 | 4LKA001AR/4KCL999CQ-C-02 | U1000R2V | 5G1.5 | 20 | X 062 15 | 3 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system |  | WCC 14
|  | 5 | [5 empty] | 7
|  | 6 | [5 empty] | 8
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 56 07 | 1 | 4LKA001AR/4KCL999CQ-C-03 | U1000R2V | 5G1.5 | 20 | X 046 15 | 3 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system
|  | 5 | [5 empty] | 7 | [6 empty] | #N/A
|  | 6 | [5 empty] | 8
| X 092 07 | 14 |  |  |  |  | X 121 07 | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 081 06 | 1 | 4LKA001AR/4KCL999CQ-C-04 | U1000R2V | 5G1.5 | 20 | X 059 06 | 1 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system
|  | 2 | [5 empty] | 3
|  | 3 | [5 empty] | 5 | [6 empty] | #N/A
|  | 4 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 082 06 | 1 | 4LKA001AR/4KCL999CQ-C-05 | U1000R2V | 5G1.5 | 35 | X 067 06 | 1 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system |  | #N/A
|  | 2 | [5 empty] | 3
|  | 3 | [5 empty] | 5
|  | 4 | [5 empty] | 7 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 083 06 | 1 | 4LKA001AR/4KCL999CQ-C-06 | U1000R2V | 5G1.5 | 35 | X 051 06 | 1 | 4KCL999CQ | 24Vcc |  | 1st floor | Secondary air system
|  | 2 | [5 empty] | 3 | [6 empty] | #N/A
|  | 3 | [5 empty] | 5
|  | 4 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | X 031 14 | 1 | 4LKA001AR/4KLD001CQ-C-01 | U1000R2V | 5G1.5 | 40 | X 211 03 | 15 | 4KLD001CQ | 24Vcc |  | 1st floor | Chemical dosing station
|  | 3 | [5 empty] | 16
|  | 4 | [5 empty] | 17 | [6 empty] | #N/A
| X? | A |  |  |  |  | X 251 03 | 30
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 049 05 | 14 | 4LKA001AR/4KLD001CQ-C-02 | U1000R2V | 5G1.5 | 40 | X 211 03 | 18 | 4KLD001CQ | 230Vac |  | 1st floor | Water steam |  | WCC 14
|  | 15 | [5 empty] | 19
|  | A | [5 empty] | 45
|  | A | [5 empty] | 46 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 073 10 | 5 | 4LKA001AR/4KLD001CQ-C-03 | U1000R2V | 12G1.5 | 40 | X 211 03 | 20 | 4KLD001CQ | 230Vac |  | 1st floor | Water steam
|  | 6 | [5 empty] | 21 | [6 empty] | #N/A
|  | 5 | [5 empty] | 1
|  | 6 | [5 empty] | 2
|  | 5 | [5 empty] | 5 | [6 empty] | #N/A
|  | 6 | [5 empty] | 6
47
[8 empty] | 48 | [6 empty] | #N/A
49
50
[8 empty] | 51 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 074 06 | 5 | 4LKA001AR/4KLD001CQ-C-04 | U1000R2V | 12G1.5 | 40 | X 211 03 | 22 | 4KLD001CQ | 230Vac |  | 1st floor | Water steam
|  | 6 | [5 empty] | 23 | [6 empty] | #N/A
|  | 5 | [5 empty] | 3
|  | 6 | [5 empty] | 4
|  | 5 | [5 empty] | 7 | [6 empty] | #N/A
|  | 6 | [5 empty] | 8
51
[8 empty] | 52 | [6 empty] | #N/A
53
54
[8 empty] | 55 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR |  |  | 4LKA001AR/4LGA005DJ-C-01 | U1000R2V | 3G1.5 | 40 |  |  | 4LGA005DJ | 24Vcc |  | 1st floor to HV room | Drain & Vent
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKA001AR | X 033 05 | 1 | 4LKA001AR/4LKA001TR-C-01 | U1000R2V | 12G1.5 | 0 | X? |  | 4LKA001TR | 24Vcc |  | 1st to 2nd floor
|  | 2 | [12 empty] | #N/A
3
4
|  | 8 | [12 empty] | #N/A
13
14
|  | 15 | [12 empty] | #N/A
X?
#N/A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | QB 044 05 | 2 | 4LKA001AR/4LKD001AR-B-01 | U1000R2V | 1x120 | 20 | IG 031 05 | 2 | 4LKD001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (NORMALE) L1 | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 044 05 | 4 | 4LKA001AR/4LKD001AR-B-02 | U1000R2V | 1x120 | 20 | IG 031 05 | 4 | 4LKD001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (NORMALE) L2 | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 044 05 | 6 | 4LKA001AR/4LKD001AR-B-03 | U1000R2V | 1x120 | 20 | IG 031 05 | 6 | 4LKD001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (NORMALE) L3 | 1st to 2nd floor |  | PRIO | WCC 22
4LKA001AR | PE | PE | 4LKA001AR/4LKD001AR-B-04 | U1000R2V | 1x70 | 20 | PE | PE | 4LKD001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION CHAUDIÈRE (NORMALE) PE | 1st to 2nd floor |  | PRIO
4LKA001AR | X? | ? | 4LKA001AR/4LKD001AR-S-01 | PROFIBUS CABLE |  | 34 | X 084 13 | 1 | 4LKD001AR |  |  | 1st to 2nd floor
|  | ? | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE
4LKA001AR | QB 070 05 | 2 | 4LKA001AR/4LKE001AR-B-01 | U1000R2V | 1x70 | 30 |  |  | 4LKE001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 1 L1 | 1st to 3rd floor |  | PRIO
4LKA001AR | QB 070 05 | 4 | 4LKA001AR/4LKE001AR-B-02 | U1000R2V | 1x70 | 30 |  |  | 4LKE001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 1 L2 | 1st to 3rd floor |  | PRIO | WCC 18
4LKA001AR | QB 070 05 | 6 | 4LKA001AR/4LKE001AR-B-03 | U1000R2V | 1x70 | 30 |  |  | 4LKE001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 1 L3 | 1st to 3rd floor |  | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4LKE001AR-B-04 | U1000R2V | 1x35 | 30 |  |  | 4LKE001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 1 PE | 1st to 3rd floor |  | PRIO
4LKA001AR | QB 071 05 | 2 | 4LKA001AR/4LKE002AR-B-01 | U1000R2V | 1x70 | 30 |  |  | 4LKE002AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 2 L1 | 1st to 3rd floor |  | PRIO | WCC 18
4LKA001AR | QB 071 05 | 4 | 4LKA001AR/4LKE002AR-B-02 | U1000R2V | 1x70 | 30 |  |  | 4LKE002AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 2 L2 | 1st to 3rd floor |  | PRIO
4LKA001AR | QB 071 05 | 6 | 4LKA001AR/4LKE002AR-B-03 | U1000R2V | 1x70 | 30 |  |  | 4LKE002AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 2 L3 | 1st to 3rd floor |  | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4LKE002AR-B-04 | U1000R2V | 1x35 | 30 |  |  | 4LKE002AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE PONT ROULANT 2 PE | 1st to 3rd floor |  | PRIO | WCC 14
4LKA001AR | X |  | 4LKA001AR/4LKF002AR-C-01 | U1000R2V | 12G1.5 | 35 | X 103 11 | 1 | 4LKF002AR | 48Vca |  | 1st to 2nd floor
2
[8 empty] | 3 | [6 empty] | #N/A
4
5
[8 empty] | 6 | [6 empty] | #N/A
7
8
#N/A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKA001AR | QB 045 05 | 2 | 4LKA001AR/4LKG001AR-B-01 | U1000R2V | 1x35 | 10 | X? |  | 4LKG001AR | 400Vca |  | 1st floor (condensate battery)
4LKA001AR | QB 045 05 | 4 | 4LKA001AR/4LKG001AR-B-02 | U1000R2V | 1x35 | 10 | X? |  | 4LKG001AR | 400Vca |  | 1st floor (condensate battery)
4LKA001AR | QB 045 05 | 6 | 4LKA001AR/4LKG001AR-B-03 | U1000R2V | 1x35 | 10 | X? |  | 4LKG001AR | 400Vca |  | 1st floor (condensate battery) |  |  | WCC 14
4LKA001AR | PE | PE | 4LKA001AR/4LKG001AR-B-04 | U1000R2V | 1x35 | 10 | PE | PE | 4LKG001AR | 400Vca |  | 1st floor (condensate battery)
4LKA001AR | QB 042 05 | 2 | 4LKA001AR/4LKJ001AR-B-01 | U1000R2V | 1x150 | 20 |  | U | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L1 | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 042 05 | 2 | 4LKA001AR/4LKJ001AR-B-02 | U1000R2V | 1x150 | 20 | U | U | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L1 | 1st to 2nd floor |  | PRIO | WCC 22
4LKA001AR | QB 042 05 | 4 | 4LKA001AR/4LKJ001AR-B-03 | U1000R2V | 1x150 | 20 | V | V | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L2 | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 042 05 | 4 | 4LKA001AR/4LKJ001AR-B-04 | U1000R2V | 1x150 | 20 | V | V | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L2 | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 042 05 | 6 | 4LKA001AR/4LKJ001AR-B-05 | U1000R2V | 1x150 | 20 | W | W | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L3 | 1st to 2nd floor |  | PRIO | WCC 22
4LKA001AR | QB 042 05 | 6 | 4LKA001AR/4LKJ001AR-B-06 | U1000R2V | 1x150 | 20 | W | W | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES L3 | 1st to 2nd floor |  | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4LKJ001AR-B-07 | U1000R2V | 1x150 | 20 | PE | PE | 4LKJ001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BASSE TENSION TRAITEMENT DES FUMÉES PE | 1st to 2nd floor |  | PRIO
4LKA001AR | QB 041 05 | 2 | 4LKA001AR/4LKK001AR-B-01 | U1000R2V | 1x120 | 17 |  | U | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L1 | 1st floor |  | PRIO | WCC 22
4LKA001AR | QB 041 05 | 2 | 4LKA001AR/4LKK001AR-B-02 | U1000R2V | 1x120 | 17 | U | U | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L1 | 1st floor |  | PRIO
4LKA001AR | QB 041 05 | 4 | 4LKA001AR/4LKK001AR-B-03 | U1000R2V | 1x120 | 17 | V | V | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L2 | 1st floor |  | PRIO
4LKA001AR | QB 041 05 | 4 | 4LKA001AR/4LKK001AR-B-04 | U1000R2V | 1x120 | 17 | V | V | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L2 | 1st floor |  | PRIO | WCC 22
4LKA001AR | QB 041 05 | 6 | 4LKA001AR/4LKK001AR-B-05 | U1000R2V | 1x120 | 17 | W | W | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L3 | 1st floor |  | PRIO
4LKA001AR | QB 041 05 | 6 | 4LKA001AR/4LKK001AR-B-06 | U1000R2V | 1x120 | 17 | W | W | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE L3 | 1st floor |  | PRIO
4LKA001AR | PE | PE | 4LKA001AR/4LKK001AR-B-07 | U1000R2V | 1x120 | 17 | PE | PE | 4LKK001AR | 400Vca | ALIMENTATION PRINCIPALE ARMOIRE BATTERIE DE PRÉCHAUFFAGE PE | 1st floor |  | PRIO | WCC 22
4LKA001AR |  |  | 4LKA001AR/4LKP001AR-B-01 | CR1-C1 | 4x25 | 100 |  |  | 4LKP001AR | 400Vca
#N/A
| PE | PE
4LKA001AR | P 084 13 | + | 4LKA001AR/P 084 13 | PROFIBUS CABLE |  |  | X 084 13 | 1 | P 084 13 | 24Vcc
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE
4LKD001AR | X 038 08 | 4 | 4LKD001AR/4LKA001AR-S-01 | PROFIBUS CABLE |  | 25 | X 084 13 | 2 | 4LKA001AR |  |  | 1st to 2nd floor | Communication
|  | 3 | [5 empty] | 1 | [6 empty] | #N/A
4LKD001AR | X 038 08 | 2 | 4LKD001AR/4LKJ001AR-S-01 | PROFIBUS CABLE |  | 30 |  |  | 4LKJ001AR |  |  | 2nd floor | Communication
1
4LKD002AR | X 094 13 | 1 | 4LKD002AR/4FDR005BJ-B-01 | U1000R2V | 4G2.5 | 60 |  | L1 | 4FDR005BJ | 400Vca |  | 2nd floor to outside | Ash system |  | WCC 14
|  | 2 | [5 empty] | L2
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 089 05 | 1 | 4LKD002AR/4FES002MO-B-01 | U1000R2V | 4G2.5 | 52 | M13 |  | 4FES002MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 090 09 | 1 | 4LKD002AR/4FES002MO-C-01 | U1000R2V | 5G1.5 | 52 | X1 | 3 | 4FES002MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 092 06 | 3 | 4LKD002AR/4FES002MO-C-02 | U1000R2V | 3G1.5 | 52 | X1 | 5 | 4FES002MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 084 05 | 1 | 4LKD002AR/4FES004MO-B-01 | U1000R2V | 4G2.5 | 73 | M12 |  | 4FES004MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 085 09 | 1 | 4LKD002AR/4FES004MO-C-01 | U1000R2V | 5G1.5 | 73 | X1 | 3 | 4FES004MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 087 06 | 3 | 4LKD002AR/4FES004MO-C-02 | U1000R2V | 3G1.5 | 73 | X1 | 5 | 4FES004MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 8 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 094 09 | 1 | 4LKD002AR/4FES005MO-B-01 | U1000R2V | 4G2.5 | 60 |  | L1 | 4FES005MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [5 empty] | L2
|  | 3 | [5 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 111 04 | 7 | 4LKD002AR/4FES005MO-C-01 | U1000R2V | 5G1.5 | 60 |  |  | 4FES005MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 8 | [12 empty] | #N/A
9
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD002AR | X 095 09 | 1 | 4LKD002AR/4FES100BC-B-01 | U1000R2V | 4G2.5 | 80 |  | L1 | 4FES100BC | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [5 empty] | L2
|  | 3 | [5 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 094 04 | 1 | 4LKD002AR/4FGO101CR-B-01 | U1000R2V | 4G6 | 20 |  | L1 | 4FGO101CR | 400Vca |  | 2nd to 3rd floor | Ash system
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 085 09 | 5 | 4LKD002AR/4KLD002CQ-C-01 | U1000R2V | 12G1.5 | 15 | X 211 03 | 19 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system |  | #N/A
|  | 6 | [5 empty] | 20
|  | 10 | [5 empty] | 21
| X 090 09 | 5 | [5 empty] | 22 | [6 empty] | #N/A
|  | 6 | [5 empty] | 23
|  | 10 | [5 empty] | 24
| XS 125 03 | 9 |  |  |  |  | X 251 03 | 10 | [6 empty] | #N/A
|  | 10 | [5 empty] | 11
|  | 11 | [5 empty] | 12
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 111 04 | 1 | 4LKD002AR/4LCA003HSS-C-01 | U1000R2V | 5G1.5 | 60 | S303 |  | 4LCA003HSS | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
3
2
|  | 4 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 112 04 | 1 | 4LKD002AR/4LCA201HSS-C-01 | U1000R2V | 3G1.5 | 70 | S303 |  | 4LCA201HSS | 24Vcc |  | 2nd floor to outside | Ash system
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 112 04 | 2 | 4LKD002AR/4LCA502HSS-C-01 | U1000R2V | 3G1.5 | 80 | S303 |  | 4LCA502HSS | 24Vcc |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 095 04 | 1 | 4LKD002AR/4SAR200BC-B-01 | U1000R2V | 4G2.5 | 75 |  | L1 | 4SAR200BC | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 082 08 | 1 | 4LKD002AR/4SDX001PO-C-01 | U1000R2V | 5G1.5 | 100 |  |  | 4SDX001PO | 48Vca |  | 2nd floor to outside | Thermal water treatment |  | WCC 14
4
2
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKD002AR | X 083 06 | 3 | 4LKD002AR/4SDX001PO-C-02 | U1000R2V | 3G1.5 | 100 |  |  | 4SDX001PO | 24Vcc |  | 2nd floor to outside | Thermal water treatment
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 184 05 | 1 | 4LKD003AR/4FDR009MO-B-01 | U1000R2V | 4G2.5 | 60 | M | L1 | 4FDR009MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 184 09 | 1 | 4LKD003AR/4FDR009MO-C-01 | U1000R2V | 5G1.5 | 60 | X1 | 3 | 4FDR009MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 7 | [5 empty] | 14
|  | 2 | [5 empty] | 12 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 187 06 | 3 | 4LKD003AR/4FDR009MO-C-02 | U1000R2V | 3G1.5 | 60 | X1 | 5 | 4FDR009MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 8 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 162 05 | 1 | 4LKD003AR/4FES008MO-B-01 | U1000R2V | 4G25 | 55 | M61 |  | 4FES008MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 163 09 | 1 | 4LKD003AR/4FES008MO-C-01 | U1000R2V | 5G1.5 | 55 | X1 | 3 | 4FES008MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
[8 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 165 06 | 3 | 4LKD003AR/4FES008MO-C-02 | U1000R2V | 3G1.5 | 55 | X1 | 5 | 4FES008MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 15 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 169 05 | 1 | 4LKD003AR/4FES038MO-B-01 | U1000R2V | 4G2.5 | 67 | M21 |  | 4FES038MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 170 09 | 1 | 4LKD003AR/4FES038MO-C-01 | U1000R2V | 5G1.5 | 67 | X1 | 3 | 4FES038MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 172 06 | 3 | 4LKD003AR/4FES038MO-C-02 | U1000R2V | 3G1.5 | 67 | X1 | 5 | 4FES038MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 9 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 174 05 | 1 | 4LKD003AR/4FES040MO-B-01 | U1000R2V | 4G2.5 | 57 | M22 |  | 4FES040MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 175 09 | 1 | 4LKD003AR/4FES040MO-C-01 | U1000R2V | 5G1.5 | 57 | X1 |  | 4FES040MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 177 06 | 3 | 4LKD003AR/4FES040MO-C-02 | U1000R2V | 3G1.5 | 57 | X1 | 5 | 4FES040MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 9 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 179 05 | 1 | 4LKD003AR/4FES050MO-B-01 | U1000R2V | 4G2.5 | 68 | M23 |  | 4FES050MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 180 09 | 1 | 4LKD003AR/4FES050MO-C-01 | U1000R2V | 5G1.5 | 68 | X1 | 3 | 4FES050MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 182 06 | 3 | 4LKD003AR/4FES050MO-C-02 | U1000R2V | 3G1.5 | 68 | X1 | 5 | 4FES050MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 8 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 163 09 | 5 | 4LKD003AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 211 03 | 27 | 4KLD002CQ | 24Vcc |  | 2nd floor
|  | 6 | [5 empty] | 28 | [6 empty] | #N/A
|  | 10 | [5 empty] | 29
| X 170 09 | 5 | [5 empty] | 30
|  | 6 | [5 empty] | 31 | [6 empty] | #N/A
|  | 8 | [5 empty] | 32
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 175 09 | 5 | 4LKD003AR/4KLD002CQ-C-02 | U1000R2V | 12G1.5 | 15 | X 211 03 | 35 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | #N/A
|  | 6 | [5 empty] | 36
|  | 8 | [5 empty] | 37
|  | 5 | [5 empty] | 40 | [6 empty] | #N/A
|  | 6 | [5 empty] | 41
|  | 10 | [5 empty] | 42
|  | 5 | [5 empty] | 31 | [6 empty] | #N/A
|  | 6 | [5 empty] | 32
|  | 10 | [5 empty] | 33
|  | 11 | [5 empty] | 26 | [6 empty] | #N/A
|  | 12 | [5 empty] | 27
| PE | PE |  |  |  |  | PE | PE
4LKD003AR | X 170 09 | 9 | 4LKD003AR/4KLD002CQ-C-03 | U1000R2V | 7G1.5 | 15 | X 211 03 | 33 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | WCC 14
|  | 10 | [5 empty] | 34
|  | 9 | [5 empty] | 38
|  | 10 | [5 empty] | 39 | [6 empty] | #N/A
|  | 13 | [5 empty] | 28
|  | 14 | [5 empty] | 29
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 253 09 | 13 | 4LKD004AR/4FAF065VAR-C-01 | U1000R2V | 3G1.5 | 25 |  |  | 4FAF065VAR | 24Vcc |  | 1st to 2nd floor | Primary air system
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 267 05 | 1 | 4LKD004AR/4FES010MO-B-01 | U1000R2V | 4G2.5 | 60 | M34 |  | 4FES010MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD004AR | X 268 09 | 1 | 4LKD004AR/4FES010MO-C-01 | U1000R2V | 5G1.5 | 60 | X1 | 3 | 4FES010MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 270 06 | 3 | 4LKD004AR/4FES010MO-C-02 | U1000R2V | 3G1.5 | 60 | X1 | 5 | 4FES010MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 8 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 257 05 | 1 | 4LKD004AR/4FES012MO-B-01 | U1000R2V | 4G2.5 | 66 | M32 |  | 4FES012MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD004AR | X 258 09 | 1 | 4LKD004AR/4FES012MO-C-01 | U1000R2V | 5G1.5 | 66 | X1 | 3 | 4FES012MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 260 06 | 3 | 4LKD004AR/4FES012MO-C-02 | U1000R2V | 3G1.5 | 66 | X1 | 5 | 4FES012MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 262 05 | 1 | 4LKD004AR/4FES014MO-B-01 | U1000R2V | 4G2.5 | 60 | M33 |  | 4FES014MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD004AR | X 263 09 | 1 | 4LKD004AR/4FES014MO-C-01 | U1000R2V | 5G1.5 | 60 | X1 | 3 | 4FES014MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 265 06 | 3 | 4LKD004AR/4FES014MO-C-02 | U1000R2V | 3G1.5 | 60 | X1 | 5 | 4FES014MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 252 02 | 1 | 4LKD004AR/4FES024MO-B-01 | U1000R2V | 4G2.5 | 50 | M31 |  | 4FES024MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD004AR | X 253 09 | 1 | 4LKD004AR/4FES024MO-C-01 | U1000R2V | 5G1.5 | 50 | X1 | 3 | 4FES024MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 255 06 | 3 | 4LKD004AR/4FES024MO-C-02 | U1000R2V | 3G1.5 | 50 | X1 | 5 | 4FES024MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD004AR | X 253 09 | 5 | 4LKD004AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 211 03 | 43 | 4KLD002CQ | 24Vcc |  |  | Ash system
|  | 6 | [5 empty] | 44
|  | 12 | [5 empty] | 45 | [6 empty] | #N/A
| X 258 09 | 5 | [5 empty] | 46
|  | 6 | [5 empty] | 47
|  | 12 | [5 empty] | 48 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD004AR | X 263 09 | 5 | 4LKD004AR/4KLD002CQ-C-02 | U1000R2V | 12G1.5 | 15 | X 211 03 | 49 | 4KLD002CQ | 48Vca |  | 2nd floor | Ash system
|  | 6 | [5 empty] | 50 | [6 empty] | #N/A
|  | 12 | [5 empty] | 51
|  | 5 | [5 empty] | 52
|  | 6 | [5 empty] | 53 | [6 empty] | #N/A
|  | 12 | [5 empty] | 54
|  | 9 | [5 empty] | 44
|  | 10 | [5 empty] | 45 | [6 empty] | #N/A
|  | 11 | [5 empty] | 46
|  | 12 | [5 empty] | 47
|  | 13 | [5 empty] | 48 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 352 05 | 1 | 4LKD005AR/4FES016MO-B-01 | U1000R2V | 4G2.5 | 66 | M43 |  | 4FES016MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 353 09 | 1 | 4LKD005AR/4FES016MO-C-01 | U1000R2V | 5G1.5 | 66 | X1 | 3 | 4FES016MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 355 06 | 3 | 4LKD005AR/4FES016MO-C-02 | U1000R2V | 3G1.5 | 66 | X1 | 5 | 4FES016MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 357 05 | 1 | 4LKD005AR/4FES018MO-B-01 | U1000R2V | 4G2.5 | 68 | M53 |  | 4FES018MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 358 09 | 1 | 4LKD005AR/4FES018MO-C-01 | U1000R2V | 5G1.5 | 68 | X1 | 3 | 4FES018MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 360 06 | 3 | 4LKD005AR/4FES018MO-C-02 | U1000R2V | 3G1.5 | 68 | X1 | 5 | 4FES018MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 342 05 | 1 | 4LKD005AR/4FES042MO-B-01 | U1000R2V | 4G2.5 | 62 | M41 |  | 4FES042MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 343 09 | 1 | 4LKD005AR/4FES042MO-C-01 | U1000R2V | 5G1.5 | 62 | X1 | 3 | 4FES042MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
12
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 345 06 | 3 | 4LKD005AR/4FES042MO-C-02 | U1000R2V | 3G1.5 | 62 | X1 | 5 | 4FES042MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 9 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 347 05 | 1 | 4LKD005AR/4FES044MO-B-01 | U1000R2V | 4G2.5 | 65 | M42 |  | 4FES044MO | 400Vca |  | 2nd floor to outside | Ash system
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 348 09 | 1 | 4LKD005AR/4FES044MO-C-01 | U1000R2V | 5G1.5 | 65 | X1 | 3 | 4FES044MO | 48Vca |  | 2nd floor to outside | Ash system |  | WCC 14
4
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 350 06 | 3 | 4LKD005AR/4FES044MO-C-02 | U1000R2V | 3G1.5 | 65 | X1 | 5 | 4FES044MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 9 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 343 09 | 5 | 4LKD005AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 215 03 | 1 | 4KLD002CQ | 24Vcc |  | 2nd floor
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
|  | 8 | [5 empty] | 3
| X 348 09 | 5 | [5 empty] | 6
|  | 6 | [5 empty] | 7 | [6 empty] | #N/A
|  | 8 | [5 empty] | 8
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 353 09 | 5 | 4LKD005AR/4KLD002CQ-C-02 | U1000R2V | 12G1.5 | 17 | X 215 03 | 11 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | #N/A
|  | 6 | [5 empty] | 12
|  | 10 | [5 empty] | 13
[8 empty] | 14 | [6 empty] | #N/A
15
16
|  | 19 | [5 empty] | 61 | [6 empty] | #N/A
|  | 20 | [5 empty] | 62
|  | 21 | [5 empty] | 63
|  | 22 | [5 empty] | 64 | [6 empty] | #N/A
|  | 23 | [5 empty] | 65
| PE | PE |  |  |  |  | PE | PE
4LKD005AR | X 343 09 | 9 | 4LKD005AR/4KLD002CQ-C-03 | U1000R2V | 7G1.5 | 17 | X 215 03 | 4 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | WCC 14
|  | 10 | [5 empty] | 5
|  | 9 | [5 empty] | 9
|  | 10 | [5 empty] | 10 | [6 empty] | #N/A
|  | 24 | [5 empty] | 66
|  | 25 | [5 empty] | 67
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 432 05 | 1 | 4LKD006AR/4FES020MO-B-01 | U1000R2V | 4G2.5 | 70 | M62 |  | 4FES020MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 433 09 | 1 | 4LKD006AR/4FES020MO-C-01 | U1000R2V | 5G1.5 | 70 | X1 | 3 | 4FES020MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 435 06 | 3 | 4LKD006AR/4FES020MO-C-02 | U1000R2V | 3G1.5 | 70 | X1 | 5 | 4FES020MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 437 05 | 1 | 4LKD006AR/4FES022MO-B-01 | U1000R2V | 4G2.5 | 74 | M63 |  | 4FES022MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 438 09 | 1 | 4LKD006AR/4FES022MO-C-01 | U1000R2V | 5G1.5 | 74 | X1 | 3 | 4FES022MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 440 06 | 3 | 4LKD006AR/4FES022MO-C-02 | U1000R2V | 3G1.5 | 74 | X1 | 5 | 4FES022MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 7 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 422 05 | 1 | 4LKD006AR/4FES046MO-B-01 | U1000R2V | 4G2.5 | 69 | M51 |  | 4FES046MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 423 09 | 1 | 4LKD006AR/4FES046MO-C-01 | U1000R2V | 5G1.5 | 69 | X1 | 3 | 4FES046MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 425 06 | 6 | 4LKD006AR/4FES046MO-C-02 | U1000R2V | 3G1.5 | 69 | X1 | 5 | 4FES046MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 11 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 427 05 | 1 | 4LKD006AR/4FES048MO-B-01 | U1000R2V | 4G2.5 | 74 | M52 |  | 4FES048MO | 400Vca |  | 2nd floor to outside | Ash system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 428 09 | 1 | 4LKD006AR/4FES048MO-C-01 | U1000R2V | 5G1.5 | 74 | X1 | 3 | 4FES048MO | 48Vca |  | 2nd floor to outside | Ash system
|  | 4 | [12 empty] | #N/A
|  | 2 | [5 empty] | 12
|  | 7 | [5 empty] | 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 430 06 | 3 | 4LKD006AR/4FES048MO-C-02 | U1000R2V | 3G1.5 | 74 | X1 | 5 | 4FES048MO | 24Vcc |  | 2nd floor to outside | Ash system
|  | 9 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD006AR | X 423 09 | 5 | 4LKD006AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 215 03 | 17 | 4KLD002CQ | 24Vcc |  | 2nd floor
|  | 6 | [5 empty] | 18
|  | 8 | [5 empty] | 19 | [6 empty] | #N/A
| X 428 09 | 5 | [5 empty] | 22
|  | 6 | [5 empty] | 23
|  | 8 | [5 empty] | 24 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 423 09 | 9 | 4LKD006AR/4KLD002CQ-C-02 | U1000R2V | 7G1.5 | 19 | X 215 03 | 20 | 4KLD002CQ | 48Vca |  | 2nd floor
|  | 10 | [5 empty] | 21 | [6 empty] | #N/A
|  | 9 | [5 empty] | 25
|  | 10 | [5 empty] | 26
|  | 18 | [5 empty] | 81 | [6 empty] | #N/A
|  | 19 | [5 empty] | 82
| PE | PE |  |  |  |  | PE | PE
4LKD006AR | X 433 09 | 5 | 4LKD006AR/4KLD002CQ-C-03 | U1000R2V | 12G1.5 | 19 | X 215 03 | 27 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | #N/A
|  | 6 | [5 empty] | 28
|  | 12 | [5 empty] | 29
|  | 5 | [5 empty] | 30 | [6 empty] | #N/A
|  | 6 | [5 empty] | 31
|  | 12 | [5 empty] | 32
|  | 20 | [5 empty] | 83 | [6 empty] | #N/A
|  | 21 | [5 empty] | 84
|  | 22 | [5 empty] | 85
|  | 23 | [5 empty] | 86 | [6 empty] | #N/A
|  | 24 | [5 empty] | 87
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | TA 512 08 | U2 | 4LKD007AR/4CTE063PO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 69 | M1 |  | 4CTE063PO | 400Vca |  | 2nd floor to outside | Cooling water system |  | #N/A
V2
W2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | TA 514 08 | U2 | 4LKD007AR/4CTE064PO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 69 | M1 |  | 4CTE064PO | 400Vca |  | 2nd floor to outside | Cooling water system
V2
|  | W2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 516 05 | 5 | 4LKD007AR/4ERF264CA-C-01 | U1000R2V | 5G1.5 | 56 |  |  | 4ERF264CA | 48Vca |  | 2nd floor to outside | Chemical dosing station
|  | 29 | [12 empty] | #N/A
33
32
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 518 05 | 5 | 4LKD007AR/4ERF269CA-C-01 | U1000R2V | 5G1.5 | 56 |  |  | 4ERF269CA | 48Vca |  | 2nd floor to outside | Chemical dosing station
29
|  | 33 | [12 empty] | #N/A
32
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 516 05 | 4 | 4LKD007AR/4FGO003CA-C-01 | U1000R2V | 5G1.5 | 80 |  |  | 4FGO003CA | 48Vca |  | 2nd floor to outside | Burner |  | WCC 14
1
5
|  | 4 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | TA 519 08 | U2 | 4LKD007AR/4FGO003MO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 80 | M1 |  | 4FGO003MO | 400Vca |  | 2nd floor to outside | Burner
|  | V2 | [12 empty] | #N/A
W2
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 518 05 | 4 | 4LKD007AR/4FGO004CA-C-01 | U1000R2V | 5G1.5 | 80 |  |  | 4FGO004CA | 48Vca |  | 2nd floor to outside | Burner |  | WCC 14
1
5
|  | 4 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | TA 520 08 | U2 | 4LKD007AR/4FGO004MO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 80 | M1 |  | 4FGO004MO | 400Vca |  | 2nd floor to outside | Burner
|  | V2 | [12 empty] | #N/A
W2
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 555 04 | 4 | 4LKD007AR/4FGO101CR-C-01 | U1000R2V | 3G1.5 | 25 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner |  | WCC 14
7
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 558 04 | 4 | 4LKD007AR/4FGO101CR-C-02 | U1000R2V | 3G1.5 | 25 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner |  | WCC 14
7
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 569 05 | 2 | 4LKD007AR/4FGO101CR-C-03 | U1000R2V | 3G1.5 | 25 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner |  | WCC 14
3
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 571 05 | 2 | 4LKD007AR/4FGO101CR-C-04 | U1000R2V | 3G1.5 | 25 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner |  | WCC 14
3
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 557 09 | 1 | 4LKD007AR/4FGO101CR-M-01 | 04IP09EISF | 4x2x0.88 | 25 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner |  | WCC 18
2
1
|  | 2 | [12 empty] | #N/A
1
2
|  | 3 | [12 empty] | #N/A
4
[7 empty] | PE | PE
4LKD007AR | X 522 09 | 5 | 4LKD007AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 211 03 | 13 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system |  | WCC 14
|  | 6 | [5 empty] | 14
| X 525 09 | 5 | [5 empty] | 17
|  | 6 | [5 empty] | 18 | [6 empty] | #N/A
| PE | 4 |  |  |  |  | X 251 03 | 55
|  | 5 | [5 empty] | 56
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR |  |  | 4LKD007AR/4KLD002CQ-C-02 | U1000R2V | 7G1.5 | 21 | X 219 03 | 38 | 4KLD002CQ | 48Vca |  | 2nd floor
39
[8 empty] | 42 | [6 empty] | #N/A
43
|  | 5 | [5 empty] | 88
|  | 6 | [5 empty] | 89 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 585 04 | 1 | 4LKD007AR/4LCA004HSS-C-01 | U1000R2V | 5G1.5 | 80 | S303 |  | 4LCA004HSS | 48Vca |  | 2nd floor to outside | Chemical dosing station
|  | 3 | [12 empty] | #N/A
2
4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | TA 511 08 | U2 | 4LKD007AR/4SDX001PO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 |  | M1 |  | 4SDX001PO | 400Vca |  | 2nd floor to outside | Thermal water treatment
V2
|  | W2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 516 05 | 2 | 4LKD007AR/4SEO209CA-C-01 | U1000R2V | 5G1.5 | 120 |  |  | 4SEO209CA | 48Vca |  | 2nd floor to outside | Drain & Vent
|  | 23 | [12 empty] | #N/A
27
26
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 521 05 | 1 | 4LKD007AR/4SEO209PO-B-01 | U1000R2V | 4G2.5 | 120 | M22 |  | 4SEO209PO | 400Vca |  | 2nd floor to outside | Drain & Vent
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 522 09 | 1 | 4LKD007AR/4SEO209PO-C-01 | U1000R2V | 5G1.5 | 120 | S 156 08.1 |  | 4SEO209PO | 48Vca |  | 2nd floor to outside | Drain & Vent
|  | 4 | [12 empty] | #N/A
2
7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 523 06 | 3 | 4LKD007AR/4SEO209PO-C-02 | U1000R2V | 3G1.5 | 120 | S 156 08 |  | 4SEO209PO | 24Vcc |  | 2nd floor to outside | Drain & Vent
6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 545 05 | 3 | 4LKD007AR/4SEO209PO-M-01 | 01IP09EGSF | 1x2x0.88 | 120 |  | 2R1 | 4SEO209PO | 24Vcc |  | 2nd floor to outside | Drain & Vent
|  | 4 | [5 empty] | 2R2
[7 empty] | PE | PE | [6 empty] | #N/A
4LKD007AR | X 518 05 | 2 | 4LKD007AR/4SEO213CA-C-01 | U1000R2V | 5G1.5 | 120 |  |  | 4SEO213CA | 48Vca |  | 2nd floor to outside | Drain & Vent
23
|  | 27 | [12 empty] | #N/A
26
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 527 05 | 1 | 4LKD007AR/4SEO213PO-B-01 | U1000R2V | 4G2.5 | 120 | M22 |  | 4SEO213PO | 400Vca |  | 2nd floor to outside | Drain & Vent |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 528 09 | 1 | 4LKD007AR/4SEO213PO-C-01 | U1000R2V | 5G1.5 | 120 | S 156 08.1 |  | 4SEO213PO | 48Vca |  | 2nd floor to outside | Drain & Vent
4
|  | 2 | [12 empty] | #N/A
7
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 529 06 | 3 | 4LKD007AR/4SEO213PO-C-02 | U1000R2V | 3G1.5 | 120 | S 156 08 |  | 4SEO213PO | 24Vcc |  | 2nd floor to outside | Drain & Vent |  | WCC 14
6
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 549 05 | 3 | 4LKD007AR/4SEO213PO-M-01 | 01IP09EGSF | 1x2x0.88 | 120 |  | 2R1 | 4SEO213PO | 24Vcc |  | 2nd floor to outside | Drain & Vent |  | WCC 14
|  | 4 | [5 empty] | 2R2
[7 empty] | PE | PE
4LKD007AR | X 542 05 | 1 | 4LKD007AR/4SEO264PO-B-01 | U1000R2V | 4G2.5 | 56 | M22 |  | 4SEO264PO | 400Vca |  | 2nd floor to outside | Drain & Vent |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | X 525 09 | 1 | 4LKD007AR/4SEO264PO-C-01 | U1000R2V | 5G1.5 | 56 | S 156 08 |  | 4SEO264PO | 48Vca |  | 2nd floor to outside | Drain & Vent
4
|  | 2 | [12 empty] | #N/A
7
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 531 09 | 1 | 4LKD007AR/4SEO269PO-C-01 | U1000R2V | 5G1.5 | 56 | S 156 08.1 |  | 4SEO269PO | 48Vca |  | 2nd floor to outside | Drain & Vent |  | WCC 14
4
2
|  | 7 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | X 532 06 | 3 | 4LKD007AR/4SEO269PO-C-02 | U1000R2V | 3G1.5 | 56 | S 156 08 |  | 4SEO269PO | 24Vcc |  | 2nd floor to outside | Drain & Vent
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | QB 511 09 |  | 4LKD007AR/TA51108-B-01 | U1000R2V | 4G6 | 2 | TA 511 08 | L1 | TA51108 | 400Vca
[8 empty] | L2 | [6 empty] | #N/A
L3
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | QB 512 09 |  | 4LKD007AR/TA51208-B-01 | U1000R2V | 4G6 | 2 | TA 512 08 | L1 | TA51208 | 400Vca |  |  |  |  | #DIV/0!
L2
L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | QB 513 09 |  | 4LKD007AR/TA51308-B-01 | U1000R2V | 4G6 | 2 | TA 513 08 | L1 | TA51308 | 400Vca
L2
[8 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | QB 514 09 |  | 4LKD007AR/TA51408-B-01 | U1000R2V | 4G6 | 2 | TA 514 08 | L1 | TA51408 | 400Vca
[8 empty] | L2 | [6 empty] | #N/A
L3
| PE | PE |  |  |  |  | PE | PE
4LKD007AR | QB 519 09 |  | 4LKD007AR/TA51908-B-01 | U1000R2V | 4G6 | 2 | TA 519 08 | L1 | TA51908 | 400Vca |  |  |  |  | #DIV/0!
L2
L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKD007AR | QB 520 09 |  | 4LKD007AR/TA52008-B-01 | U1000R2V | 4G6 | 2 | TA 520 08 | L1 | TA52008 | 400Vca
L2
[8 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE001BC | X | L1 | 4LKE001BC/Q02204_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02204_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE001BC | X | L2 | 4LKE001BC/Q02204_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02204_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE001BC | X | L3 | 4LKE001BC/Q02204_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02204_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE011BC | X | L1 | 4LKE011BC/Q02304_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02304_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE011BC | X | L2 | 4LKE011BC/Q02304_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02304_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE011BC | X | L3 | 4LKE011BC/Q02304_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02304_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE021BC | X | L1 | 4LKE021BC/Q02404_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02404_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE021BC | X | L2 | 4LKE021BC/Q02404_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02404_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE021BC | X | L3 | 4LKE021BC/Q02404_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02404_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE031BC | X | L1 | 4LKE031BC/Q02504_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02504_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE031BC | X | L2 | 4LKE031BC/Q02504_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02504_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE031BC | X | L3 | 4LKE031BC/Q02504_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02504_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE041BC | X | L1 | 4LKE041BC/Q02604_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02604_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE041BC | X | L2 | 4LKE041BC/Q02604_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02604_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE041BC | X | L3 | 4LKE041BC/Q02604_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02604_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE051BC | X | L1 | 4LKE051BC/Q02704_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02704_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE051BC | X | L2 | 4LKE051BC/Q02704_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02704_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE051BC | X | L3 | 4LKE051BC/Q02704_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02704_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE061BC | X | L1 | 4LKE061BC/Q02804_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02804_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE061BC | X | L2 | 4LKE061BC/Q02804_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02804_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE061BC | X | L3 | 4LKE061BC/Q02804_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02804_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE071BC | X | L1 | 4LKE071BC/Q02904_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q02904_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE071BC | X | L2 | 4LKE071BC/Q02904_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q02904_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE071BC | X | L3 | 4LKE071BC/Q02904_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q02904_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE081BC | X | L1 | 4LKE081BC/Q03004_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q03004_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE081BC | X | L2 | 4LKE081BC/Q03004_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q03004_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE081BC | X | L3 | 4LKE081BC/Q03004_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q03004_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE091BC | X | L1 | 4LKE091BC/Q03104_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q03104_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE091BC | X | L2 | 4LKE091BC/Q03104_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q03104_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE091BC | X | L3 | 4LKE091BC/Q03104_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q03104_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE101BC | X | L1 | 4LKE101BC/Q03204_L1-B-01 | U1000R2V | 3G1.5 | 30 | X | L | Q03204_L1 | 400Vca
|  | N1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE101BC | X | L2 | 4LKE101BC/Q03204_L2-B-01 | U1000R2V | 3G1.5 | 50 | X | L | Q03204_L2 | 400Vca
|  | N2 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKE101BC | X | L3 | 4LKE101BC/Q03204_L3-B-01 | U1000R2V | 3G1.5 | 70 | X | L | Q03204_L3 | 400Vca
|  | N3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF001AR | XA 515 05 | 1 | 4LKF001AR/4LKF006AR-B-01 | U1000R2V | 3G2.5 | 15 | D 034 01 |  | 4LKF006AR | 230Vca |  | 2nd floor
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF001AR | XA 517 05 | 1 | 4LKF001AR/4LKF006AR-B-02 | U1000R2V | 3G2.5 | 15 | D 035 01 |  | 4LKF006AR | 230Vca |  | 2nd floor
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF001AR | XB 516 05 | 1 | 4LKF001AR/4LKF006AR-B-03 | U1000R2V | 3G2.5 | 15 | D 036 01 |  | 4LKF006AR | 230Vca |  | 2nd floor
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF001AR | XB 518 05 | 1 | 4LKF001AR/4LKF006AR-B-04 | U1000R2V | 3G2.5 | 15 | D 037 01 |  | 4LKF006AR | 230Vca |  | 2nd floor
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 091 04 | 1 | 4LKF002AR/4CRF152AR-B-01 | U1000R2V | 4G6 | 62 |  | L1 | 4CRF152AR | 400Vca |  | 2nd floor to outside
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 092 13 | 1 | 4LKF002AR/4CTE065AR-B-01 | U1000R2V | 4G4 | 68 |  | L1 | 4CTE065AR | 400Vca |  | 2nd floor to outside |  |  | WCC 14
|  | 2 | [5 empty] | L2
|  | 3 | [5 empty] | L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF002AR | X 092 09 | 1 | 4LKF002AR/4CTE066AR-B-01 | U1000R2V | 4G4 | 71 |  | L1 | 4CTE066AR | 400Vca |  | 2nd floor to outside | Water steam
|  | 2 | [5 empty] | L2
|  | 3 | [5 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 092 04 | 1 | 4LKF002AR/4CTE111CR-B-01 | U1000R2V | 3G1.5 | 68 |  | L1 | 4CTE111CR | 400Vca |  | 2nd floor to outside | Water steam
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 082 05 | 1 | 4LKF002AR/4DEM071MO-B-01 | U1000R2V | 4G2.5 | 48 | M11 |  | 4DEM071MO | 400Vca |  | 2nd floor to outside | Water steam
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 083 09 | 1 | 4LKF002AR/4DEM071MO-C-01 | U1000R2V | 5G1.5 | 48 |  |  | 4DEM071MO | 48Vca |  | 2nd floor to outside | Water steam |  | WCC 14
4
2
|  | 7 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 084 06 | 3 | 4LKF002AR/4DEM071MO-C-02 | U1000R2V | 3G1.5 | 48 |  |  | 4DEM071MO | 24Vcc |  | 2nd floor to outside | Water steam
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 085 05 | 1 | 4LKF002AR/4FGR484MO-B-01 | U1000R2V | 4G2.5 | 39 | M12 |  | 4FGR484MO | 400Vca |  | 2nd floor to outside | Water steam
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 086 09 | 1 | 4LKF002AR/4FGR484MO-C-01 | U1000R2V | 5G1.5 | 39 |  |  | 4FGR484MO | 48Vca |  | 2nd floor to outside | Water steam |  | WCC 14
4
2
|  | 7 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 087 06 | 3 | 4LKF002AR/4FGR484MO-C-02 | U1000R2V | 3G1.5 | 39 |  |  | 4FGR484MO | 24Vcc |  | 2nd floor to outside | Water steam
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 088 05 | 1 | 4LKF002AR/4FGR494ZV-B-01 | U1000R2V | 4G2.5 | 39 | M13 |  | 4FGR494ZV | 400Vca |  | 2nd floor to outside | Water steam
|  | 2 | [12 empty] | #N/A
3
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 089 09 | 1 | 4LKF002AR/4FGR494ZV-C-01 | U1000R2V | 5G1.5 | 39 |  |  | 4FGR494ZV | 48Vca |  | 2nd floor to outside | Water steam |  | WCC 14
4
2
|  | 7 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 090 06 | 3 | 4LKF002AR/4FGR494ZV-C-02 | U1000R2V | 3G1.5 | 39 |  |  | 4FGR494ZV | 24Vcc |  | 2nd floor to outside | Water steam
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 083 09 | 5 | 4LKF002AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 219 03 | 15 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system
|  | 6 | [5 empty] | 16 | [6 empty] | #N/A
| X 086 09 | 5 | [5 empty] | 17
|  | 6 | [5 empty] | 18
| X? | ?? | [5 empty] | 34 | [6 empty] | #N/A
|  | ?? | [5 empty] | 35
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 171 04 | 1 | 4LKF002AR/4LCA001HSS-C-01 | U1000R2V | 5G1.5 | 30 | S303 |  | 4LCA001HSS | 48Vca |  | 2nd floor to outside | Water steam |  | WCC 14
2
3
|  | 4 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF002AR | X 101 04 | 1 | 4LKF002AR/4LCA002HSS-C-01 | U1000R2V | 5G1.5 | 30 | S303 |  | 4LCA002HSS | 48Vca |  | 2nd floor to outside | Water steam
|  | 2 | [12 empty] | #N/A
3
4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF002AR | X 104 04 | 1 | 4LKF002AR/4LCA101HSS-C-01 | U1000R2V | 3G1.5 | 30 | S303 |  | 4LCA101HSS | 48Vca |  | 2nd floor to outside | Water steam
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF002AR | X 104 04 | 2 | 4LKF002AR/4LCA102HSS-C-01 | U1000R2V | 3G1.5 | 30 | S303 |  | 4LCA102HSS | 48Vca |  | 2nd floor to outside | Water steam
4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 158 05 | 1 | 4LKF003AR/4DEM055MO-B-01 | U1000R2V | 4G2.5 | 45 | M23 |  | 4DEM055MO | 400Vca |  | 2nd floor to outside | Ash removal system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 159 09 | 1 | 4LKF003AR/4DEM055MO-C-01 | U1000R2V | 5G1.5 | 45 |  |  | 4DEM055MO | 48Vca |  | 2nd floor to outside | Ash removal system
|  | 4 | [12 empty] | #N/A
2
7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 161 06 | 3 | 4LKF003AR/4DEM055MO-C-02 | U1000R2V | 3G1.5 | 45 |  |  | 4DEM055MO | 24Vcc |  | 2nd floor to outside | Ash removal system
6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 163 05 | 1 | 4LKF003AR/4FGR146MO-B-01 | U1000R2V | 4G2.5 | 50 | M24 |  | 4FGR146MO | 400Vca |  | 2nd floor to outside | Ash removal system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 164 09 | 1 | 4LKF003AR/4FGR146MO-C-01 | U1000R2V | 5G1.5 | 50 |  |  | 4FGR146MO | 48Vca |  | 2nd floor to outside | Ash removal system
|  | 4 | [12 empty] | #N/A
2
7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 165 06 | 3 | 4LKF003AR/4FGR146MO-C-02 | U1000R2V | 3G1.5 | 50 | S 164 08 |  | 4FGR146MO | 24Vcc |  | 2nd floor to outside | Ash removal system
6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 166 05 | 1 | 4LKF003AR/4FGR493ZV-B-01 | U1000R2V | 4G2.5 | 39 | M25 |  | 4FGR493ZV | 400Vca |  | 2nd floor to outside | Ash removal system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 167 09 | 1 | 4LKF003AR/4FGR493ZV-C-01 | U1000R2V | 5G1.5 | 39 |  |  | 4FGR493ZV | 48Vca |  | 2nd floor to outside | Ash removal system
|  | 4 | [12 empty] | #N/A
2
7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 168 06 | 3 | 4LKF003AR/4FGR493ZV-C-02 | U1000R2V | 3G1.5 | 39 |  |  | 4FGR493ZV | 24Vcc |  | 2nd floor to outside | Ash removal system
6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 152 05 | 1 | 4LKF003AR/4FGR496MO-B-01 | U1000R2V | 4G2.5 | 39 | M21 |  | 4FGR496MO | 400Vca |  | 2nd floor to outside | Ash removal system
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 153 09 | 1 | 4LKF003AR/4FGR496MO-C-01 | U1000R2V | 5G1.5 | 39 |  |  | 4FGR496MO | 48Vca |  | 2nd floor to outside | Ash removal system
|  | 4 | [12 empty] | #N/A
2
7
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 154 06 | 3 | 4LKF003AR/4FGR496MO-C-02 | U1000R2V | 3G1.5 | 39 | S 153 08 |  | 4FGR496MO | 24Vcc |  | 2nd floor to outside | Ash removal system
6
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 159 09 | 5 | 4LKF003AR/4KLD002CQ-C-01 | U1000R2V | 12G1.5 | 15 | X 219 03 | 19 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system
|  | 6 | [5 empty] | 20
|  | 8 | [5 empty] | 21 | [6 empty] | #N/A
| X 153 09 | 5 | [5 empty] | 22
|  | 6 | [5 empty] | 23
| X 164 09 | 5 | [5 empty] | 24 | [6 empty] | #N/A
|  | 6 | [5 empty] | 25
| X? | ?? | [5 empty] | 36
|  | ?? | [5 empty] | 37 | [6 empty] | #N/A
| XS 185 03 | 8 |  |  |  |  | X 251 03 | 69
|  | 9 | [5 empty] | 70
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 172 11 | 1 | 4LKF003AR/4LKA001AR-C-01 | U1000R2V | 5G1.5 | 35 |  |  | 4LKA001AR | 48Vca |  | 1st to 2nd floor | Water steam
2
|  | 3 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 530 50 | 1 | 4LKF003AR/4SEO269PO-B-01 | U1000R2V | 4G2.5 | 55 | M22 |  | 4SEO269PO | 400Vca |  | 2nd floor to outside | Drain & Vent |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF003AR | X 156 09 | 1 | 4LKF003AR/4SEO269PO-C-01 | U1000R2V | 5G1.5 | 55 | S 156 08.1 |  | 4SEO269PO | 48Vca |  | 2nd floor to outside | Drain & Vent
4
|  | 2 | [12 empty] | #N/A
7
| PE | PE |  |  |  |  | PE | PE
4LKF003AR | X 157 06 | 3 | 4LKF003AR/4SEO269PO-C-02 | U1000R2V | 3G1.5 | 55 | S 156 08 |  | 4SEO269PO | 24Vcc |  | 2nd floor to outside | Drain & Vent |  | WCC 14
6
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 225 05 | 1 | 4LKF004AR/4DEM066MO-B-01 | U1000R2V | 4G2.5 | 55 | M32 |  | 4DEM066MO | 400Vca |  | 2nd floor to outside | Ash removal system |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF004AR | X 226 09 | 1 | 4LKF004AR/4DEM066MO-C-01 | U1000R2V | 5G1.5 | 55 |  |  | 4DEM066MO | 48Vca |  | 2nd floor to outside | Ash removal system
4
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 228 06 | 3 | 4LKF004AR/4DEM066MO-C-02 | U1000R2V | 3G1.5 | 55 |  |  | 4DEM066MO | 24Vcc |  | 2nd floor to outside | Ash removal system |  | WCC 14
9
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 230 05 | 1 | 4LKF004AR/4FGR160MO-B-01 | U1000R2V | 4G2.5 | 48 | M33 |  | 4FGR160MO | 400Vca |  | 2nd floor to outside | Ash removal system |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF004AR | X 231 09 | 1 | 4LKF004AR/4FGR160MO-C-01 | U1000R2V | 5G1.5 | 48 | S 231 08,1 |  | 4FGR160MO | 48Vca |  | 2nd floor to outside | Ash removal system
4
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 232 26 | 5 | 4LKF004AR/4FGR160MO-C-02 | U1000R2V | 3G1.5 | 48 |  |  | 4FGR160MO | 24Vcc |  | 2nd floor to outside | Ash removal system |  | WCC 14
7
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 233 05 | 1 | 4LKF004AR/4FGR492ZV-B-01 | U1000R2V | 4G2.5 | 39 | M34 |  | 4FGR492ZV | 400Vca |  | 2nd floor to outside | Ash removal system |  | WCC 14
2
3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF004AR | X 234 09 | 1 | 4LKF004AR/4FGR492ZV-C-01 | U1000R2V | 5G1.5 | 39 |  |  | 4FGR492ZV | 48Vca |  | 2nd floor to outside | Ash removal system
4
|  | 2 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 235 06 | 3 | 4LKF004AR/4FGR492ZV-C-02 | U1000R2V | 3G1.5 | 39 |  |  | 4FGR492ZV | 24Vcc |  | 2nd floor to outside | Ash removal system |  | WCC 14
6
| PE | PE |  |  |  |  | PE | PE
4LKF004AR | X 226 09 | 5 | 4LKF004AR/4KLD002CQ-C-01 | U1000R2V | 12G1.5 | 15 | X 219 03 | 26 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system |  | #N/A
|  | 6 | [5 empty] | 27
|  | 12 | [5 empty] | 28
| X 231 09 | 5 | [5 empty] | 29 | [6 empty] | #N/A
|  | 6 | [5 empty] | 30
| X? | ?? | [5 empty] | 40
|  | ?? | [5 empty] | 41 | [6 empty] | #N/A
| XS 255 03 | 7 |  |  |  |  | X 251 03 | 78
|  | 8 | [5 empty] | 79
|  | 9 | [5 empty] | 80 | [6 empty] | #N/A
|  | 8 | [5 empty] | 81
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 296 05 | 5 | 4LKF005AR/4CRE189CA-C-01 | U1000R2V | 5G1.5 | 46 |  |  | 4CRE189CA | 48Vca |  | 2nd floor to outside | Condensate system |  | WCC 14
29
32
|  | 33 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | TA 292 08 | U2 | 4LKF005AR/4CRE189MO-B-01 | 2XSLCYK-JB EMV-UV | 3x35/16 | 46 | M1 |  | 4CRE189MO | 400Vca |  | 2nd floor to outside | Condensate system
|  | V2 | [12 empty] | #N/A
W2
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 298 05 | 5 | 4LKF005AR/4CRE196CA-C-01 | U1000R2V | 5G1.5 | 46 |  |  | 4CRE196CA | 48Vca |  | 2nd floor to outside | Condensate system |  | WCC 14
29
34
|  | 33 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | TA 294 08 | U2 | 4LKF005AR/4CRE196MO-B-01 | 2XSLCYK-JB EMV-UV | 3x35/16 | 46 | M1 |  | 4CRE196MO | 400Vca |  | 2nd floor to outside | Condensate system
|  | V2 | [12 empty] | #N/A
W2
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 296 05 | 2 | 4LKF005AR/4EBA014CA-C-01 | U1000R2V | 5G1.5 | 183 |  |  | 4EBA014CA | 48Vca |  | 2nd floor to outside | Condensate system |  | WCC 14
23
26
|  | 27 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | TA 291 08 | U2 | 4LKF005AR/4EBA014PO-B-01 | 2XSLCYK-JB EMV-UV | 3x35/16 | 183 | M1 |  | 4EBA014PO | 400Vca |  | 2nd floor to outside | Condensate system
|  | V2 | [12 empty] | #N/A
W2
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 323 05 | 3 | 4LKF005AR/4EBA014PO-M-01 | 08IP09EISF | 8x2x0.88 | 183 |  | 1R1 | 4EBA014PO | 24Vcc |  | 2nd floor to outside | Condensate system |  | WCC 26
|  | 4 | [5 empty] | 1R2
|  | 5 | [5 empty] | 2R1
|  | 6 | [5 empty] | 2R2 | [6 empty] | #N/A
|  | 7 | [5 empty] | 3R1
|  | 8 | [5 empty] | 3R2
|  | 9 | [5 empty] | 4 | [6 empty] | #N/A
|  | 10 | [5 empty] | 6
|  | 11 | [5 empty] | 5
|  | 13 | [5 empty] | 4 | [6 empty] | #N/A
|  | 14 | [5 empty] | 6
|  | 15 | [5 empty] | 5
|  | 17 | [5 empty] | 1+ | [6 empty] | #N/A
|  | 18 | [5 empty] | 2-
|  | 19 | [5 empty] | 1+
|  | 20 | [5 empty] | 2- | [6 empty] | #N/A
4LKF005AR | X 298 05 | 2 | 4LKF005AR/4EBA043CA-C-01 | U1000R2V | 5G1.5 | 185 |  |  | 4EBA043CA | 48Vca |  | 2nd floor to outside | Condensate system
23
|  | 26 | [12 empty] | #N/A
27
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | TA 293 08 | U2 | 4LKF005AR/4EBA043PO-B-01 | 2XSLCYK-JB EMV-UV | 3x35/16 | 185 | M1 |  | 4EBA043PO | 400Vca |  | 2nd floor to outside | Condensate system |  | #N/A
V2
W2
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF005AR | X 331 05 | 3 | 4LKF005AR/4EBA043PO-M-01 | 08IP09EISF | 8x2x0.88 | 185 |  | 1R1 | 4EBA043PO | 24Vcc |  | 2nd floor to outside | Condensate system
|  | 4 | [5 empty] | 1R2
|  | 5 | [5 empty] | 2R1 | [6 empty] | #N/A
|  | 6 | [5 empty] | 2R2
|  | 7 | [5 empty] | 3R1
|  | 8 | [5 empty] | 3R2 | [6 empty] | #N/A
|  | 9 | [5 empty] | 4
|  | 10 | [5 empty] | 6
|  | 11 | [5 empty] | 5 | [6 empty] | #N/A
|  | 13 | [5 empty] | 4
|  | 14 | [5 empty] | 6
|  | 15 | [5 empty] | 5 | [6 empty] | #N/A
|  | 17 | [5 empty] | 1+
|  | 18 | [5 empty] | 2-
|  | 19 | [5 empty] | 1+ | [6 empty] | #N/A
|  | 20 | [5 empty] | 2-
4LKF005AR | X 298 05 | 30 | 4LKF005AR/4FTA049VAR-C-01 | U1000R2V | 3G1.5 | 10 | X 033 05 | 27 | 4FTA049VAR | 48Vca |  | 1st to 2nd floor | Secondary air system
[7 empty] | X 091 04 | 9 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 296 05 | 24 | 4LKF005AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 211 03 | 1 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system
|  | 25 | [5 empty] | 2 | [6 empty] | #N/A
|  | 30 | [5 empty] | 5
|  | 31 | [5 empty] | 6
| X 391 03 | 5 |  |  |  |  | X 251 03 | 82 | [6 empty] | #N/A
|  | 6 | [5 empty] | 83
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 321 04 | 4 | 4LKF005AR/4KLD002CQ-C-02 | U1000R2V | 7G1.5 | 10 | X 211 03 | 3 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | WCC 14
|  | 7 | [5 empty] | 4
|  | 4 | [5 empty] | 7
|  | 7 | [5 empty] | 8 | [6 empty] | #N/A
|  | 7 | [5 empty] | 134
|  | 8 | [5 empty] | 135
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF005AR | X 296 05 | 24 | 4LKF005AR/4KLD002CQ-C-03 | U1000R2V | 7G1.5 | 10 | X 219 03 | 44 | 4KLD002CQ | 48Vca |  | 2nd floor
|  | 25 | [5 empty] | 45
|  | 30 | [5 empty] | 3 | [6 empty] | #N/A
|  | 31 | [5 empty] | 4
|  | 5 | [5 empty] | 136
|  | 6 | [5 empty] | 137 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 321 04 | 4 | 4LKF005AR/4KLD002CQ-C-04 | U1000R2V | 7G1.5 | 10 | X 219 03 | 1 | 4KLD002CQ | 48Vca |  | 2nd floor
|  | 7 | [5 empty] | 2 | [6 empty] | #N/A
|  | 4 | [5 empty] | 5
|  | 7 | [5 empty] | 6
|  | 7 | [5 empty] | 138 | [6 empty] | #N/A
|  | 8 | [5 empty] | 139
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | L1 |  | 4LKF005AR/4LKF006AR-C-01 | U1000R2V | 4G50 | 10 | L1 |  | 4LKF006AR | 24Vcc |  | 2nd floor |  |  | #DIV/0!
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF005AR | XB 372 03 | 1 | 4LKF005AR/4LKF006AR-C-02 | U1000R2V | 7G1.5 | 10 | XB 592 03 | 1 | 4LKF006AR | 24Vcc |  | 2nd floor
|  | 2 | [5 empty] | 5
|  | 3 | [5 empty] | 6 | [6 empty] | #N/A
|  | 4 | [5 empty] | 1
|  | 5 | [5 empty] | 5
|  | 6 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF005AR | X 365 04 | 1 | 4LKF005AR/ZONETURBINE-C-01 | U1000R2V | 5G1.5 | 185 | S303 |  | ZONETURBINE | 48Vca |  |  | Condensate system
|  | 3 | [12 empty] | #N/A
2
4
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR | TA 512 08 | U2 | 4LKF006AR/4CTE063PO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 65.1 | M1 |  | 4CTE063PO | 400Vca |  | 2nd floor to outside | Cooling water system
V2
|  | W2 | [12 empty] | #N/A
PE
PE
4LKF006AR | TA 514 08 | U2 | 4LKF006AR/4CTE064PO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 67.1 | M1 |  | 4CTE064PO | 400Vca |  | 2nd floor to outside | Cooling water system |  | #N/A
V2
W2
|  | PE | [12 empty] | #N/A
PE
4LKF006AR | X 516 05 | 5 | 4LKF006AR/4ERF264CA-C-01 | U1000R2V | 5G1.5 | 50 | X? | ? | 4ERF264CA | 24Vcc |  | 2nd floor to outside | Chemical dosing station
|  | 29 | [5 empty] | ? | [6 empty] | #N/A
|  | 33 | [5 empty] | ?
|  | 32 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR | X 518 05 | 5 | 4LKF006AR/4ERF269CA-C-01 | U1000R2V | 5G1.5 | 50 | X? | ? | 4ERF269CA | 24Vcc |  | 2nd floor to outside | Chemical dosing station
|  | 29 | [5 empty] | ?
|  | 33 | [5 empty] | ? | [6 empty] | #N/A
|  | 32 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 516 05 | 4 | 4LKF006AR/4FGO003CA-C-01 | U1000R2V | 5G1.5 | 50 | X? | ? | 4FGO003CA | 24Vcc |  | 2nd floor to outside | Burner |  | WCC 14
|  | 1 | [5 empty] | ?
|  | 5 | [5 empty] | ?
|  | 4 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | TA 519 08 | U2 | 4LKF006AR/4FGO003MO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 50 | M1 |  | 4FGO003MO | 400Vca |  | 2nd floor to outside | Burner
|  | V2 | [12 empty] | #N/A
W2
PE
|  | PE | [12 empty] | #N/A
4LKF006AR | X 518 05 | 4 | 4LKF006AR/4FGO004CA-C-01 | U1000R2V | 5G1.5 | 50 | X? | ? | 4FGO004CA | 24Vcc |  | 2nd floor to outside | Burner
|  | 1 | [5 empty] | ?
|  | 5 | [5 empty] | ? | [6 empty] | #N/A
|  | 4 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | TA 520 08 | U2 | 4LKF006AR/4FGO004MO-B-01 | 2XSLCYK-JB EMV-UV | 3x6+3x1.0 | 50 | M1 |  | 4FGO004MO | 400Vca |  | 2nd floor to outside | Burner |  | #N/A
V2
W2
|  | PE | [12 empty] | #N/A
PE
4LKF006AR | X 555 04 | 4 | 4LKF006AR/4FGO101CR-C-01 | U1000R2V | 3G1.5 | 20 | X? | ? | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 558 04 | 4 | 4LKF006AR/4FGO101CR-C-02 | U1000R2V | 3G1.5 | 20 | X? | ? | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 569 05 | 4 | 4LKF006AR/4FGO101CR-C-03 | U1000R2V | 3G1.5 | 20 | X? | ? | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 571 05 | 4 | 4LKF006AR/4FGO101CR-C-04 | U1000R2V | 3G1.5 | 20 | X? | ? | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner
|  | 7 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 557 09 | 1 | 4LKF006AR/4FGO101CR-M-01 | 04IP09EISF BU | 4x2x0.88 | 20 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor | Burner
#N/A
#N/A
2
1
[8 empty] | 2 | [6 empty] | #N/A
4LKF006AR | X 560 09 | 1 | 4LKF006AR/4FGO101CR-M-02 | 04IP09EISF BU | 4x2x0.88 | 20 |  |  | 4FGO101CR | 24Vcc |  | 2nd to 3rd floor
#N/A
|  | 2 | [12 empty] | #N/A
3
4
4LKF006AR | X? | ?? | 4LKF006AR/4KLD002CQ-C-01 | U1000R2V | 7G1.5 | 15 | X 211 03 | 9 | 4KLD002CQ | 24Vcc |  | 2nd floor |  |  | WCC 14
|  | ?? | [5 empty] | 10
| X 611 03 | 30 |  |  |  |  | X 251 03 | 118
|  | 31 | [5 empty] | 119 | [6 empty] | #N/A
|  | 32 | [5 empty] | 120
|  | 33 | [5 empty] | 121
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR |  |  | 4LKF006AR/4KLD002CQ-C-02 | U1000R2V | 7G1.5 | 15 | X 211 03 | 11 | 4KLD002CQ | 48Vca |  | 2nd floor
12
|  | 4 | [5 empty] | 187 | [6 empty] | #N/A
|  | 7 | [5 empty] | 188
|  | 7 | [5 empty] | 189
|  | 8 | [5 empty] | 190 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 518 05 | 24 | 4LKF006AR/4KLD002CQ-C-03 | U1000R2V | 7G1.5 | 15 | X 219 03 | 7 | 4KLD002CQ | 48Vca |  | 2nd floor
|  | 25 | [5 empty] | 8 | [6 empty] | #N/A
|  | 30 | [5 empty] | 11
|  | 31 | [5 empty] | 12
|  | 5 | [5 empty] | 175 | [6 empty] | #N/A
|  | 6 | [5 empty] | 176
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 547 04 | 4 | 4LKF006AR/4KLD002CQ-C-04 | U1000R2V | 7G1.5 | 15 | X 219 03 | 9 | 4KLD002CQ | 48Vca |  | 2nd floor |  |  | WCC 14
|  | 7 | [5 empty] | 10
|  | 4 | [5 empty] | 13
|  | 7 | [5 empty] | 14 | [6 empty] | #N/A
|  | 7 | [5 empty] | 178
|  | 8 | [5 empty] | 179
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR | X 585 04 | 1 | 4LKF006AR/4LCA004HSS-C-01 | U1000R2V | 5G1.5 | 20 | S303 |  | 4LCA004HSS | 24Vcc |  | 2nd floor to outside | Chemical dosing station
3
|  | 2 | [12 empty] | #N/A
4
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | X 516 05 | 2 | 4LKF006AR/4SEO209CA-C-01 | U1000R2V | 5G1.5 | 119.1 | X? | ? | 4SEO209CA | 24Vcc |  | 2nd floor to outside | Drain & Vent |  | WCC 14
|  | 23 | [5 empty] | ?
|  | 27 | [5 empty] | ?
|  | 26 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR |  |  | 4LKF006AR/4SEO209PO-M-01 | 04IP09EISF BU | 4x2x0.88 | 119.1 | X 543 05 | 3 | 4SEO209PO | 24Vcc |  | 2nd floor to outside | Drain & Vent
[8 empty] | 4 | [6 empty] | #N/A
#N/A
#N/A
4LKF006AR | X 518 05 | 2 | 4LKF006AR/4SEO213CA-C-01 | U1000R2V | 5G1.5 | 119.1 | X? | ? | 4SEO213CA | 24Vcc |  | 2nd floor to outside | Drain & Vent
|  | 23 | [5 empty] | ?
|  | 27 | [5 empty] | ? | [6 empty] | #N/A
|  | 26 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LKF006AR |  |  | 4LKF006AR/4SEO213PO-M-01 | 04IP09EISF BU | 4x2x0.88 | 118.1 | X 549 05 | 3 | 4SEO213PO | 24Vcc |  | 2nd floor to outside | Drain & Vent |  | #N/A
4
#N/A
#N/A
4LKF006AR | QB 511 09 |  | 4LKF006AR/TA51108-A-01 | U1000R2V | 4G6 | 20 | TA 511 08 | L1 | TA51108 | 400Vca
[8 empty] | L2 | [6 empty] | #N/A
L3
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | QB 512 09 |  | 4LKF006AR/TA51208-A-01 | U1000R2V | 4G6 | 20 | TA 512 08 | L1 | TA51208 | 400Vca |  |  |  |  | #DIV/0!
L2
L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR | QB 513 09 |  | 4LKF006AR/TA51308-A-01 | U1000R2V | 4G6 | 20 | TA 513 08 | L1 | TA51308 | 400Vca
L2
[8 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | QB 514 09 |  | 4LKF006AR/TA51408-A-01 | U1000R2V | 4G6 | 20 | TA 514 08 | L1 | TA51408 | 400Vca
[8 empty] | L2 | [6 empty] | #N/A
L3
| PE | PE |  |  |  |  | PE | PE
4LKF006AR | QB 519 09 |  | 4LKF006AR/TA51908-A-01 | U1000R2V | 4G6 | 20 | TA 519 08 | L1 | TA51908 | 400Vca |  |  |  |  | #DIV/0!
L2
L3
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKF006AR | QB 520 09 |  | 4LKF006AR/TA52008-A-01 | U1000R2V | 4G6 | 20 | TA 520 08 | L1 | TA52008 | 400Vca
L2
[8 empty] | L3 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKF007AR | X 526 06 | 3 | 4LKF007AR/4SEO264PO-C-02 | U1000R2V | 3G1.5 | 56 | S 156 08 |  | 4SEO264PO | 24Vcc |  | 2nd floor to outside | Drain & Vent
|  | 6 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 014 09 | 2 | 4LKM001AR/4DCA001CA-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA001CA | 230Vca |  |  | Drain & Vent
|  | 3 | [12 empty] | #N/A
4
1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 014 09 | 2 | 4LKM001AR/4DCA002CA-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA002CA | 230Vca |  |  | Drain & Vent
3
|  | 4 | [12 empty] | #N/A
1
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 014 09 | 2 | 4LKM001AR/4DCA003CA-B-01 | U1000R2V | 5G6 | 10 |  |  | 4DCA003CA | 230Vca |  |  | Drain & Vent |  | WCC 18
3
4
|  | 1 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 020 04 | 2 | 4LKM001AR/4DCA101BC-B-01 | U1000R2V | 3G2.5 | 10 | X | L | 4DCA101BC | 230Vca |  |  | Drain & Vent
|  | 1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 020 04 | 4 | 4LKM001AR/4DCA201BC-B-01 | U1000R2V | 3G2.5 | 10 | X | L | 4DCA201BC | 230Vca |  |  | Drain & Vent
|  | 3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 020 04 | 6 | 4LKM001AR/4DCA301BC-B-01 | U1000R2V | 3G2.5 | 10 | X | L | 4DCA301BC | 230Vca |  |  | Drain & Vent
|  | 5 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 020 04 | 12 | 4LKM001AR/4EPA055PO-B-01 | U1000R2V | 3G2.5 | 13 | X |  | 4EPA055PO | 230Vca |  |  | Thermal water treatment
|  | 11 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 020 04 | 14 | 4LKM001AR/4EPA075PO-B-01 | U1000R2V | 3G2.5 | 13 | X |  | 4EPA075PO | 230Vca |  |  | Thermal water treatment
|  | 13 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 013 09 | 2 | 4LKM001AR/4FGR001CA-B-01 | U1000R2V | 5G6 | 10 |  |  | 4FGR001CA | 230Vca |  |  | Primary air system
|  | 3 | [12 empty] | #N/A
4
1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 020 04 | 8 | 4LKM001AR/4FGR065ZV-B-01 | U1000R2V | 3G2.5 | 13 | X | L | 4FGR065ZV | 230Vca |  |  | Secondary air system
|  | 7 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 020 04 | 10 | 4LKM001AR/4FGR247ZV-B-01 | U1000R2V | 3G2.5 | 10 | X |  | 4FGR247ZV | 230Vca |  |  | Flue gas recirculation system
9
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 020 04 | 16 | 4LKM001AR/4FTA049ZV-B-01 | U1000R2V | 3G2.5 | 13 | X |  | 4FTA049ZV | 230Vca |  |  | Flue gas recirculation system
15
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 030 04 | 1 | 4LKM001AR/4KLD002CQ-C-01 | U1000R2V | 12G1.5 | 15 | X 215 03 | 33 | 4KLD002CQ | 24Vcc |  | 2nd floor | Ash system
|  | 2 | [5 empty] | 34
|  | 3 | [5 empty] | 35 | [6 empty] | #N/A
|  | 4 | [5 empty] | 36
|  | 5 | [5 empty] | 37
|  | 6 | [5 empty] | 38 | [6 empty] | #N/A
|  | 7 | [5 empty] | 39
| X? | A |  |  |  |  | X 251 03 | 128
|  | A | [5 empty] | 129 | [6 empty] | #N/A
|  | A | [5 empty] | 130
|  | A | [5 empty] | 131
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 013 09 | 6 | 4LKM001AR/4LKM001CR-B-01 | U1000R2V | 5G16 | 10 | X 020 14 | 2 | 4LKM001CR | 400Vca |  | 2nd floor |  | PRIO
|  | 7 | [5 empty] | 3
|  | 8 | [5 empty] | 4 | [6 empty] | #N/A
|  | 5 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | X 014 04 | 1 | 4LKM001AR/4LKM002CR-B-01 | U1000R2V | 1x50 | 10 | X 020 04 | 1 | 4LKM002CR | 230Vca |  | 2nd floor |  |  | WCC 18
4LKM001AR | X 014 04 | 2 | 4LKM001AR/4LKM002CR-B-02 | U1000R2V | 1x50 | 10 | X 020 04 | 2 | 4LKM002CR | 230Vca |  | 2nd floor
4LKM001AR | X 014 04 | 3 | 4LKM001AR/4LKM002CR-B-03 | U1000R2V | 1x50 | 10 | X 020 04 | 3 | 4LKM002CR | 230Vca |  | 2nd floor
4LKM001AR | X 014 04 | 4 | 4LKM001AR/4LKM002CR-B-04 | U1000R2V | 1x50 | 10 | X 020 04 | 4 | 4LKM002CR | 230Vca |  | 2nd floor |  |  | WCC 18
4LKM001AR | PE | PE | 4LKM001AR/4LKM002CR-B-05 | U1000R2V | 1x50 | 10 | PE | PE | 4LKM002CR | 230Vca |  | 2nd floor
4LKM001AR | X 013 04 | 1 | 4LKM001AR/4LKM003CR-B-01 | U1000R2V | 1x35 | 15 | X |  | 4LKM003CR | 230Vca |  | 2nd floor
4LKM001AR | X 013 04 | 2 | 4LKM001AR/4LKM003CR-B-02 | U1000R2V | 1x35 | 15 | X |  | 4LKM003CR | 230Vca |  | 2nd floor |  |  | WCC 14
4LKM001AR | X 013 04 | 3 | 4LKM001AR/4LKM003CR-B-03 | U1000R2V | 1x35 | 15 | X |  | 4LKM003CR | 230Vca |  | 2nd floor
4LKM001AR | X 013 04 | 4 | 4LKM001AR/4LKM003CR-B-04 | U1000R2V | 1x35 | 15 | X |  | 4LKM003CR | 230Vca |  | 2nd floor
4LKM001AR | PE | PE | 4LKM001AR/4LKM003CR-B-05 | U1000R2V | 1x35 | 15 | X |  | 4LKM003CR | 230Vca |  | 2nd floor |  |  | WCC 14
4LKM001AR | X 013 04 | 2 | 4LKM001AR/4LKM004CR-B-01 | U1000R2V | 5G2.5 | 10 | X |  | 4LKM004CR | 230Vca |  | 1st to 2nd floor
3
|  | 4 | [12 empty] | #N/A
1
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | IG 020 14 | 2 | 4LKM001AR/4LMA001AR-B-01 | U1000R2V | 5G70 | 20 | IG 020 14 | 2 | 4LMA001AR | 400Vca |  | 2nd floor |  |  | WCC 38
|  | 4 | [5 empty] | 4
|  | 6 | [5 empty] | 6
|  | 8 | [5 empty] | 8 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | Q 012 14 |  | 4LKM001AR/4UPS001LD-B-01 | U1000R2V | 5G70 | 25 | X40 | L1 | 4UPS001LD | 230Vca |  | 2nd floor |  | PRIO
[8 empty] | L2 | [6 empty] | #N/A
L3
N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | Q 026 04 |  | 4LKM001AR/4UPS001LD-B-02 | U1000R2V | 5G70 | 25 | X10 | L1 | 4UPS001LD | 230Vca |  | 2nd floor |  | PRIO
L2
[8 empty] | L3 | [6 empty] | #N/A
N
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | Q 012 09 |  | 4LKM001AR/4UPS002LD-B-01 | U1000R2V | 5G70 | 45 | X40 | L1 | 4UPS002LD | 230Vca |  | 2nd to 3rd floor |  | PRIO | WCC 38
L2
L3
[8 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001AR | Q 026 09 |  | 4LKM001AR/4UPS002LD-B-02 | U1000R2V | 5G70 | 45 | X10 | L1 | 4UPS002LD | 230Vca |  | 2nd to 3rd floor |  | PRIO
[8 empty] | L2 | [6 empty] | #N/A
L3
N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001AR | X 015 09 | 6 | 4LKM001AR/PLATFORM-B-01 | U1000R2V | 5G2.5 | 10 | X1 | L1 | PLATFORM | 230Vca
|  | 7 | [5 empty] | L2
|  | 8 | [5 empty] | L3 | [6 empty] | #N/A
|  | 5 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 2 | 4LKM001CR/4LKE001BC-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4LKE001BC | 230Vca |  |  |  |  | WCC 18
|  | 3 | [5 empty] | L2
|  | 4 | [5 empty] | L3
|  | 1 | [5 empty] | N1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 036 04 | 8 | 4LKM001CR/4LKE002BC-B-01 | U1000R2V | 3G2.5 | 30 | X | L | 4LKE002BC | 230Vca
|  | 7 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 036 04 | 10 | 4LKM001CR/4LKE003BC-B-01 | U1000R2V | 3G2.5 | 30 | X | L | 4LKE003BC | 230Vca
|  | 9 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 036 04 | 12 | 4LKM001CR/4LKE004BC-B-01 | U1000R2V | 3G4 | 30 | X | L | 4LKE004BC | 230Vca
|  | 11 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 6 | 4LKM001CR/4LKE011BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE011BC | 230Vca
|  | 7 | [5 empty] | L2 | [6 empty] | #N/A
|  | 8 | [5 empty] | L3
|  | 5 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 04 | 10 | 4LKM001CR/4LKE021BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE021BC | 230Vca
|  | 11 | [5 empty] | L2
|  | 12 | [5 empty] | L3 | [6 empty] | #N/A
|  | 9 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 14 | 4LKM001CR/4LKE031BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE031BC | 230Vca |  |  |  |  | WCC 18
|  | 15 | [5 empty] | L2
|  | 16 | [5 empty] | L3
|  | 13 | [5 empty] | N1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 18 | 4LKM001CR/4LKE041BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE041BC | 230Vca
|  | 19 | [5 empty] | L2 | [6 empty] | #N/A
|  | 20 | [5 empty] | L3
|  | 17 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 04 | 22 | 4LKM001CR/4LKE051BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE051BC | 230Vca
|  | 23 | [5 empty] | L2
|  | 24 | [5 empty] | L3 | [6 empty] | #N/A
|  | 21 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 26 | 4LKM001CR/4LKE061BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE061BC | 230Vca |  |  |  |  | WCC 18
|  | 27 | [5 empty] | L2
|  | 28 | [5 empty] | L3
|  | 25 | [5 empty] | N1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 30 | 4LKM001CR/4LKE071BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE071BC | 230Vca
|  | 31 | [5 empty] | L2 | [6 empty] | #N/A
|  | 32 | [5 empty] | L3
|  | 29 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 04 | 34 | 4LKM001CR/4LKE081BC-C-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE081BC | 230Vca
|  | 35 | [5 empty] | L2
|  | 36 | [5 empty] | L3 | [6 empty] | #N/A
|  | 33 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 38 | 4LKM001CR/4LKE091BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE091BC | 230Vca |  |  |  |  | WCC 18
|  | 39 | [5 empty] | L2
|  | 40 | [5 empty] | L3
|  | 37 | [5 empty] | N1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 022 04 | 42 | 4LKM001CR/4LKE101BC-B-01 | U1000R2V | 5G6 | 30 | X | L1 | 4LKE101BC | 230Vca
|  | 43 | [5 empty] | L2 | [6 empty] | #N/A
|  | 44 | [5 empty] | L3
|  | 41 | [5 empty] | N1
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 036 04 | 2 | 4LKM001CR/4LKE102BC-B-01 | U1000R2V | 3G2.5 | 30 | X | L | 4LKE102BC | 230Vca
|  | 1 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 036 04 | 4 | 4LKM001CR/4LKE202BC-B-01 | U1000R2V | 3G2.5 | 30 | X | L | 4LKE202BC | 230Vca
|  | 3 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 036 04 | 6 | 4LKM001CR/4LKE302BC-B-01 | U1000R2V | 3G2.5 | 30 | X | L | 4LKE302BC | 230Vca
|  | 5 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 039 09 | 2 | 4LKM001CR/4LKM001CA-B-01 | U1000R2V | 7G1.5 | 10 | X 051 03 | 1 | 4LKM001CA | 230Vca
|  | 17 | [5 empty] | 2
|  | 18 | [5 empty] | 3 | [6 empty] | #N/A
|  | 19 | [5 empty] | 4
|  | 20 | [5 empty] | 5
|  | 21 | [5 empty] | 6 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR | X 039 09 | 25 | 4LKM001CR/4LKM003CR-B-01 | U1000R2V | 5G1.5 | 10 |  |  | 4LKM003CR | 230Vca
|  | 26 | [12 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 039 09 | 27 | 4LKM001CR/4LKN001AR-B-01 | U1000R2V | 5G1.5 | 10 |  |  | 4LKN001AR | 230Vca
28
#N/A
| PE | PE |  |  |  |  | PE | PE
4LKM001CR |  |  | 4LKM001CR/EXT-C-01 | BIRTFLEX 5111-PVC-PUR-JB | 4G0.75 | 10 |  |  | EXT | 230Vca |  |  | Flue gas |  | WCC 14
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 2 | 4LKM001CR/Q02204_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02204_S | 230Vca
|  | 1 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 036 04 | 4 | 4LKM001CR/Q02204_S-C-01 | U1000R2V | 3G1.5 | 10 | IN | + | Q02204_S | 230Vca
|  | 3 | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 4 | 4LKM001CR/Q02304_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02304_S | 230Vca
|  | 3 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 6 | 4LKM001CR/Q02404_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02404_S | 230Vca
|  | 5 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 8 | 4LKM001CR/Q02504_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02504_S | 230Vca
|  | 7 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 10 | 4LKM001CR/Q02604_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02604_S | 230Vca
|  | 9 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 12 | 4LKM001CR/Q02704_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02704_S | 230Vca
|  | 11 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 14 | 4LKM001CR/Q02804_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02804_S | 230Vca
|  | 13 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 16 | 4LKM001CR/Q02904_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q02904_S | 230Vca
|  | 15 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 18 | 4LKM001CR/Q03004_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q03004_S | 230Vca
|  | 17 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 20 | 4LKM001CR/Q03104_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q03104_S | 230Vca
|  | 19 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001CR | X 022 10 | 22 | 4LKM001CR/Q03204_S-B-01 | U1000R2V | 3G1.5 | 10 | X | L | Q03204_S | 230Vca
|  | 21 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM001TR |  | N | 4LKM001TR/4LKM001AR-B-01 | U1000R2V | 1x240 | 10 | QB 010 04 | 2 | 4LKM001AR | 400Vca | LV DISTRIBUTION ALIMENTATION PRINCIPALE ENTRANTE N | 2nd floor |  | PRIO
4LKM001TR |  | L1 | 4LKM001TR/4LKM001AR-B-02 | U1000R2V | 1x240 | 10 | QB 010 04 | 4 | 4LKM001AR | 400Vca | LV DISTRIBUTION ALIMENTATION PRINCIPALE ENTRANTE L1 | 2nd floor |  | PRIO
4LKM001TR |  | L2 | 4LKM001TR/4LKM001AR-B-03 | U1000R2V | 1x240 | 10 | QB 010 04 | 6 | 4LKM001AR | 400Vca | LV DISTRIBUTION ALIMENTATION PRINCIPALE ENTRANTE L2 | 2nd floor |  | PRIO | WCC 30
4LKM001TR |  | L3 | 4LKM001TR/4LKM001AR-B-04 | U1000R2V | 1x240 | 10 | QB 010 04 | 8 | 4LKM001AR | 400Vca | LV DISTRIBUTION ALIMENTATION PRINCIPALE ENTRANTE L3 | 2nd floor |  | PRIO
4LKM001TR | PE | PE | 4LKM001TR/4LKM001AR-B-05 | U1000R2V | 1x120 | 10 | PE | PE | 4LKM001AR | 400Vca | LV DISTRIBUTION ALIMENTATION PRINCIPALE ENTRANTE PE | 2nd floor |  | PRIO
4LKM002CR | X 023 04 | 70 | 4LKM002CR/4DPC035CR-B-01 | U1000R2V | 5G16 | 10 | X | L1 | 4DPC035CR | 230Vca |  |  | Drain & Vent |  | WCC 22
|  | 71 | [5 empty] | L2
|  | 72 | [5 empty] | L3
|  | 69 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 031 04 | 9/PE | 4LKM002CR/4KLC001AR-E-01 | U1000R2V | 3G2.5 | 20 | X 031 04 |  | 4KLC001AR | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS |  | Primary air system
|  | 1 | [5 empty] | 5 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 1 | 4LKM002CR/4KLD001CQ-E-01 | U1000R2V | 3G2.5 | 15 | X 031 04 | 1 | 4KLD001CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 1st to 2nd floor
|  | 2 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 3 | 4LKM002CR/4KLD002CQ-E-01 | U1000R2V | 3G2.5 | 15 | X 031 04 | 1 | 4KLD002CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 2nd floor
|  | 4 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 5 | 4LKM002CR/4KLD003CQ-E-01 | U1000R2V | 3G2.5 | 15 | X 031 04 | 1 | 4KLD003CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 2nd to 3rd floor
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 7 | 4LKM002CR/4KLD004CQ-E-01 | U1000R2V | 3G2.5 | 15 | X 031 04 | 1 | 4KLD004CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 2nd to 3rd floor
|  | 8 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 9 | 4LKM002CR/4KLD005CQ-E-01 | U1000R2V | 3G2.5 | 115 | X 031 04 | 1 | 4KLD005CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 2nd floor to ABR
|  | 10 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 11 | 4LKM002CR/4KLD006CQ-E-01 | U1000R2V | 3G2.5 | 250 | X 031 04 | 1 | 4KLD006CQ | 230Vca | CHARGES DE SERVICE DES COMPARTIMENTS | 2nd floor to HV room
|  | 12 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 3 | 4LKM002CR/4LKM011BC-B-01 | U1000R2V | 5G16 | 20 | X | L1 | 4LKM011BC | 230Vca
|  | 2 | [5 empty] | L2 | [6 empty] | #N/A
|  | 4 | [5 empty] | L3
|  | 1 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 54 | 4LKM002CR/4LKM012BC-B-01 | U1000R2V | 5G16 | 20 | X | L1 | 4LKM012BC | 230Vca
|  | 55 | [5 empty] | L2
|  | 56 | [5 empty] | L3 | [6 empty] | #N/A
|  | 53 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 66 | 4LKM002CR/4LKM013BC-B-01 | U1000R2V | 5G16 | 20 | X | L1 | 4LKM013BC | 230Vca |  |  |  |  | WCC 22
|  | 67 | [5 empty] | L2
|  | 68 | [5 empty] | L3
|  | 65 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 7 | 4LKM002CR/4LKM021BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM021BC | 230Vca
|  | 6 | [5 empty] | L2 | [6 empty] | #N/A
|  | 8 | [5 empty] | L3
|  | 5 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 58 | 4LKM002CR/4LKM022BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM022BC | 230Vca
|  | 59 | [5 empty] | L2
|  | 60 | [5 empty] | L3 | [6 empty] | #N/A
|  | 57 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 10 | 4LKM002CR/4LKM031BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM031BC | 230Vca |  |  |  |  | WCC 22
|  | 11 | [5 empty] | L2
|  | 12 | [5 empty] | L3
|  | 9 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 14 | 4LKM002CR/4LKM032BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM032BC | 230Vca
|  | 15 | [5 empty] | L2 | [6 empty] | #N/A
|  | 16 | [5 empty] | L3
|  | 13 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 62 | 4LKM002CR/4LKM032BC-B-02 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM032BC | 230Vca
|  | 63 | [5 empty] | L2
|  | 64 | [5 empty] | L3 | [6 empty] | #N/A
|  | 61 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 18 | 4LKM002CR/4LKM041BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM041BC | 230Vca |  |  |  |  | WCC 22
|  | 19 | [5 empty] | L2
|  | 20 | [5 empty] | L3
|  | 17 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 22 | 4LKM002CR/4LKM051BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM051BC | 230Vca
|  | 23 | [5 empty] | L2 | [6 empty] | #N/A
|  | 24 | [5 empty] | L3
|  | 21 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 26 | 4LKM002CR/4LKM061BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM061BC | 230Vca
|  | 27 | [5 empty] | L2
|  | 28 | [5 empty] | L3 | [6 empty] | #N/A
|  | 25 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 30 | 4LKM002CR/4LKM071BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM071BC | 230Vca |  |  |  |  | WCC 22
|  | 31 | [5 empty] | L2
|  | 32 | [5 empty] | L3
|  | 29 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 34 | 4LKM002CR/4LKM081BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM081BC | 230Vca
|  | 35 | [5 empty] | L2 | [6 empty] | #N/A
|  | 36 | [5 empty] | L3
|  | 33 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 38 | 4LKM002CR/4LKM082BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM082BC | 230Vca
|  | 39 | [5 empty] | L2
|  | 40 | [5 empty] | L3 | [6 empty] | #N/A
|  | 37 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 42 | 4LKM002CR/4LKM091BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM091BC | 230Vca |  |  |  |  | WCC 22
|  | 43 | [5 empty] | L2
|  | 44 | [5 empty] | L3
|  | 41 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 023 04 | 46 | 4LKM002CR/4LKM101BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM101BC | 230Vca
|  | 47 | [5 empty] | L2 | [6 empty] | #N/A
|  | 48 | [5 empty] | L3
|  | 45 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM002CR | X 023 04 | 50 | 4LKM002CR/4LKM111BC-B-01 | U1000R2V | 5G16 | 50 | X | L1 | 4LKM111BC | 230Vca
|  | 51 | [5 empty] | L2
|  | 52 | [5 empty] | L3 | [6 empty] | #N/A
|  | 49 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM002CR | X 034 04 | 16 | 4LKM002CR/4LMA001AR-E-01 | U1000R2V | 3G2.5 | 10 | X 063 04 | 1 | 4LMA001AR | 230Vca |  |  |  |  | WCC 14
|  | 15 | [5 empty] | 7
| PE | PE |  |  |  |  | PE | PE
4LKM011BC | X | L2 | 4LKM011BC/4DPC001CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC001CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM011BC | X | L2 | 4LKM011BC/4DPC002CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC002CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM011BC | X | L2 | 4LKM011BC/4DPC003CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC003CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM012BC | X | L2 | 4LKM012BC/4DPC027CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC027CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM012BC | X | L2 | 4LKM012BC/4DPC028CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC028CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM013BC | X | L2 | 4LKM013BC/4DPC033CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC033CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM013BC | X | L2 | 4LKM013BC/4DPC034CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC034CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM021BC | X | L2 | 4LKM021BC/4DPC004CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC004CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM022BC | X | L2 | 4LKM022BC/4DPC029CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC029CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM022BC | X | L2 | 4LKM022BC/4DPC030CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC030CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM031BC | X | L2 | 4LKM031BC/4DPC005CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC005CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM031BC | X | L2 | 4LKM031BC/4DPC006CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC006CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM032BC | X | L2 | 4LKM032BC/4DPC007CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC007CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM032BC | X | L2 | 4LKM032BC/4DPC008CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC008CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM032BC | X | L2 | 4LKM032BC/4DPC031CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC031CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM032BC | X | L2 | 4LKM032BC/4DPC032CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC032CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM041BC | X | L2 | 4LKM041BC/4DPC009CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC009CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM041BC | X | L2 | 4LKM041BC/4DPC010CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC010CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM051BC | X | L2 | 4LKM051BC/4DPC011CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC011CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM051BC | X | L2 | 4LKM051BC/4DPC012CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC012CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM061BC | X | L2 | 4LKM061BC/4DPC013CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC013CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM061BC | X | L2 | 4LKM061BC/4DPC014CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC014CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM071BC | X | L2 | 4LKM071BC/4DPC015CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC015CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM071BC | X | L2 | 4LKM071BC/4DPC016CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC016CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM081BC | X | L2 | 4LKM081BC/4DPC017CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC017CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM081BC | X | L2 | 4LKM081BC/4DPC018CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC018CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM081BC | X | L2 | 4LKM081BC/4DPC019CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC019CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM081BC | X | L2 | 4LKM081BC/4DPC020CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC020CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM091BC | X | L2 | 4LKM091BC/4DPC021CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC021CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM091BC | X | L2 | 4LKM091BC/4DPC022CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC022CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM101BC | X | L2 | 4LKM101BC/4DPC023CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC023CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LKM101BC | X | L2 | 4LKM101BC/4DPC024CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC024CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2 | [6 empty] | #N/A
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4LKM111BC | X | L2 | 4LKM111BC/4DPC025CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC025CR | 230Vca |  |  | Drain & Vent
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3 | [6 empty] | #N/A
|  | N | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LKM111BC | X | L2 | 4LKM111BC/4DPC026CR-B-01 | U1000R2V | 5G6 | 10 | X | L1 | 4DPC026CR | 230Vca |  |  | Drain & Vent |  | WCC 18
|  | L1 | [5 empty] | L2
|  | L3 | [5 empty] | L3
|  | N | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 029 09 | 4 | 4LMA001AR/4CRF180BJ-B | U1000R2V | 3G6 | 10 | X | L | 4CRF180BJ | 230Vca |  |  | Flue gas
|  | 3 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 64 | 4LMA001AR/4CRF203JQI-B | U1000R2V | 3G1.5 | 10 | X | L | 4CRF203JQI | 230Vca |  |  | Cooling water system
|  | 63 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 029 09 | 2 | 4LMA001AR/4CTE100BJ-B | U1000R2V | 3G6 | 10 | X | L | 4CTE100BJ | 230Vca |  |  | Flue gas
|  | 1 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 025 04 | 6 | 4LMA001AR/4EAU001BJ-B | U1000R2V | 3G10 | 10 | X1 | L1 | 4EAU001BJ | 230Vca |  |  | Sampling station
|  | 5 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 68 | 4LMA001AR/4EBA007JQI-B | U1000R2V | 3G1.5 | 10 | X | L | 4EBA007JQI | 230Vca |  |  | Flue gas
|  | 67 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 62 | 4LMA001AR/4EBA133JQI-B | U1000R2V | 3G1.5 | 10 | X | L | 4EBA133JQI | 230Vca |  |  | Thermal water treatment
|  | 61 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 46 | 4LMA001AR/4EPA055VAR-B-01 | U1000R2V | 3G2.5 | 10 | X 032 05 | 1 | 4EPA055VAR | 230Vca |  | 1st to 2nd floor | Flue gas
|  | 45 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 058 03 | 7 | 4LMA001AR/4EPA055VAR-B-02 | U1000R2V | 3G2.5 | 10 | X 033 05 | 1 | 4EPA055VAR | 48Vca |  | 1st to 2nd floor | Flue gas
|  | 8 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 48 | 4LMA001AR/4EPA075VAR-B-01 | U1000R2V | 3G2.5 | 10 | X 032 05 | 1 | 4EPA075VAR | 230Vca |  | 1st to 2nd floor | Flue gas
|  | 47 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 21 | 4LMA001AR/4EPA075VAR-B-02 | U1000R2V | 3G2.5 | 10 | X 033 05 | 1 | 4EPA075VAR | 48Vca |  | 1st to 2nd floor | Flue gas
|  | 22 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 76 | 4LMA001AR/4ERF201PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 3 | 4ERF201PO | 230Vca |  |  | Flue gas
|  | 75 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 74 | 4LMA001AR/4ERF208PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 1 | 4ERF208PO | 230Vca |  |  | Flue gas
|  | 73 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 92 | 4LMA001AR/4ERF214PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 3 | 4ERF214PO | 230Vca |  |  | Flue gas
|  | 91 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 88 | 4LMA001AR/4ERF221PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 3 | 4ERF221PO | 230Vca |  |  | Flue gas
|  | 87 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 86 | 4LMA001AR/4ERF228PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 1 | 4ERF228PO | 230Vca |  |  | Flue gas
|  | 85 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 90 | 4LMA001AR/4ERF248PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 1 | 4ERF248PO | 230Vca |  |  | Flue gas
|  | 89 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 80 | 4LMA001AR/4ERF261PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 3 | 4ERF261PO | 230Vca |  |  | Flue gas
|  | 79 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 78 | 4LMA001AR/4ERF268PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 1 | 4ERF268PO | 230Vca |  |  | Flue gas
|  | 77 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 84 | 4LMA001AR/4ERF281PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 3 | 4ERF281PO | 230Vca |  |  | Flue gas
|  | 83 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 82 | 4LMA001AR/4ERF288PO-B-01 | U1000R2V | 3G2.5 | 10 | X1 | 1 | 4ERF288PO | 230Vca |  |  | Flue gas
|  | 81 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 42 | 4LMA001AR/4FAF065VAR-B-01 | U1000R2V | 3G2.5 | 10 | X 032 05 | 1 | 4FAF065VAR | 230Vca |  | 1st to 2nd floor | Flue gas
|  | 41 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 5 | 4LMA001AR/4FAF065VAR-B-02 | U1000R2V | 3G2.5 | 10 | X 033 05 | 1 | 4FAF065VAR | 48Vca |  | 1st to 2nd floor | Flue gas
|  | 6 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 6 | 4LMA001AR/4FES100BC-B-01 | U1000R2V | 3G2.5 | 10 | X02.30 | 1 | 4FES100BC | 230Vca |  |  | Flue gas
|  | 5 | [5 empty] | 3N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 12 | 4LMA001AR/4FGO101CR-B-01 | U1000R2V | 3G2.5 | 10 | X01 | L | 4FGO101CR | 230Vca |  | 2nd to 3rd floor | Flue gas
|  | 11 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 12 | 4LMA001AR/4FGOCR101-B-01 | U1000R2V | 3G2.5 | 40 | X01 | L | 4FGOCR101 | 400Vca |  |  | Burners and control valves
|  | 11 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 14 | 4LMA001AR/4FGR001AC-B-01 | U1000R2V | 3G2.5 | 10 | X1 | L | 4FGR001AC | 230Vca |  | 2nd floot to lift | Lift
|  | 13 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 50 | 4LMA001AR/4FGR097AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FGR097AT | 230Vca |  |  | Primary air system
|  | 49 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 52 | 4LMA001AR/4FGR099AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FGR099AT | 230Vca |  |  | Primary air system
|  | 51 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 54 | 4LMA001AR/4FGR101AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FGR101AT | 230Vca |  |  | Flue gas
|  | 53 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 38 | 4LMA001AR/4FGR372AT-B-01 | U1000R2V | 3G2.5 | 10 | X | ? | 4FGR372AT | 230Vca |  |  | Flue gas
|  | 37 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 34 | 4LMA001AR/4FSR101TV-B-01 | U1000R2V | 3G2.5 | 10 | X | ? | 4FSR101TV | 230Vca |  |  | Water steam
|  | 33 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 66 | 4LMA001AR/4FSR233JQI-B01 | U1000R2V | 3G1.5 | 10 | X | L | 4FSR233JQI | 230Vca |  |  | Flue gas
|  | 65 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 44 | 4LMA001AR/4FTA049VAR-B-01 | U1000R2V | 3G2.5 | 10 | X 032 05 | 1 | 4FTA049VAR | 230Vca |  | 1st to 2nd floor | Flue gas
|  | 43 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 19 | 4LMA001AR/4FTA049VAR-B-02 | U1000R2V | 3G2.5 | 10 | X 033 05 | 1 | 4FTA049VAR | 48Vca |  | 1st to 2nd floor | Flue gas
|  | 20 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 58 | 4LMA001AR/4FTA056AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FTA056AT | 230Vca |  |  | Flue gas
|  | 57 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 60 | 4LMA001AR/4FTA057AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FTA057AT | 230Vca |  |  | Flue gas
|  | 59 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 56 | 4LMA001AR/4FTA075AT-B-01 | U1000R2V | 3G1.5 | 10 | X | 1 | 4FTA075AT | 230Vca |  |  | Flue gas
|  | 55 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 36 | 4LMA001AR/4FTA080TV-B-01 | U1000R2V | 3G2.5 | 10 | X | ? | 4FTA080TV | 230Vca |  |  | Flue gas
|  | 35 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 72 | 4LMA001AR/4FVX005JQI-B-01 | U1000R2V | 3G1.5 | 10 | X | L | 4FVX005JQI | 230Vca |  |  | Water steam
|  | 71 | [5 empty] | N | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 162 | 4LMA001AR/4KIT001AR-B-01 | U1000R2V | 3G1.5 | 25 | X 031 03 | 2 | 4KIT001AR | 230Vca | UPS ALIMENTATION 1 | 2nd to 3rd floor
|  | 161 | [5 empty] | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 164 | 4LMA001AR/4KIT001AR-B-02 | U1000R2V | 3G1.5 | 25 | X 032 03 | 2 | 4KIT001AR | 230Vca | UPS ALIMENTATION 2 | 2nd to 3rd floor
|  | 163 |  |  |  |  | X 032 03 | 1 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 166 | 4LMA001AR/4KIT002AR-B-01 | U1000R2V | 3G1.5 | 25 | X 031 04 | 1 | 4KIT002AR | 230Vca | UPS ALIMENTATION 1 | 2nd to 3rd floor
|  | 165 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 168 | 4LMA001AR/4KIT002AR-B-02 | U1000R2V | 3G1.5 | 25 | X 031 04 | 3 | 4KIT002AR | 230Vca | UPS ALIMENTATION 2 | 2nd to 3rd floor
|  | 167 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 94 | 4LMA001AR/4KIT003AR-B-01 | U1000R2V | 3G2.5 | 20 | X 041 05 | 1 | 4KIT003AR | 400Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd to 3rd floor
|  | 93 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 96 | 4LMA001AR/4KIT003AR-B-02 | U1000R2V | 3G2.5 | 20 | X 041 05 | 3 | 4KIT003AR | 400Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd to 3rd floor
|  | 95 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 130 | 4LMA001AR/4KLC001AR-B-01 | U1000R2V | 3G2.5 | 25 | X 041 05 | 1 | 4KLC001AR | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd to 3rd floor
|  | 129 | [5 empty] | 2 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 132 | 4LMA001AR/4KLC001AR-B-02 | U1000R2V | 3G2.5 | 25 | X 041 05 | 3 | 4KLC001AR | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd to 3rd floor
|  | 131 | [5 empty] | 4 | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR |  |  | 4LMA001AR/4KLC001AR-S-01 | ProfiNET - IE FC TP Standard Cable |  | 35 |  |  | 4KLC001AR
4LMA001AR | X 026 04 | 4 | 4LMA001AR/4KLC010AR-B-01 | U1000R2V | 3G2.5 | 10 | X | ? | 4KLC010AR | 400Vca | ALIMENTATION ARMOIRE API PONTS ROULANTS | 2nd floor |  | PRIO | WCC 14
|  | 3 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 105 | 4LMA001AR/4KLD001CQ-B-01 | U1000R2V | 3G1.5 | 25 | X 041 04 | 1 | 4KLD001CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 1st to 2nd floor |  |  | WCC 14
|  | 106 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 107 | 4LMA001AR/4KLD001CQ-B-02 | U1000R2V | 3G1.5 | 25 | X 041 04 | 3 | 4KLD001CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 1st to 2nd floor |  |  | WCC 14
|  | 108 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 109 | 4LMA001AR/4KLD002CQ-B-01 | U1000R2V | 3G1.5 | 15 | X 041 04 | 1 | 4KLD002CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd floor |  |  | WCC 14
|  | 110 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 111 | 4LMA001AR/4KLD002CQ-B-02 | U1000R2V | 3G1.5 | 15 | X 041 04 | 3 | 4KLD002CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd floor |  |  | WCC 14
|  | 112 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 113 | 4LMA001AR/4KLD003CQ-B-01 | U1000R2V | 3G1.5 | 25 | X 041 04 | 1 | 4KLD003CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd to 3rd floor |  |  | WCC 14
|  | 114 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 115 | 4LMA001AR/4KLD003CQ-B-02 | U1000R2V | 3G1.5 | 25 | X 041 04 | 3 | 4KLD003CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd to 3rd floor |  |  | WCC 14
|  | 116 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR |  |  | 4LMA001AR/4KLD003CQ-B-03 | U1000R2V | 3G1.5 | 25 | X 241 10 | 2 | 4KLD003CQ | 230Vca |  | 2nd to 3rd floor |  |  | WCC 14
1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 117 | 4LMA001AR/4KLD004CQ-B-01 | U1000R2V | 3G1.5 | 25 | X 041 04 | 1 | 4KLD004CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd to 3rd floor |  |  | WCC 14
|  | 118 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 119 | 4LMA001AR/4KLD004CQ-B-02 | U1000R2V | 3G1.5 | 25 | X 041 04 | 3 | 4KLD004CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd to 3rd floor |  |  | WCC 14
|  | 120 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR |  |  | 4LMA001AR/4KLD004CQ-B-03 | U1000R2V | 3G1.5 | 25 | X 241 10 | 2 | 4KLD004CQ | 230Vca |  | 2nd to 3rd floor |  |  | WCC 14
1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 121 | 4LMA001AR/4KLD005CQ-B-01 | U1000R2V | 3G1.5 | 25 | X 041 04 | 1 | 4KLD005CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd floor to ABR |  |  | WCC 14
|  | 122 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 123 | 4LMA001AR/4KLD005CQ-B-02 | U1000R2V | 3G1.5 | 25 | X 041 04 | 3 | 4KLD005CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd floor to ABR |  |  | WCC 14
|  | 124 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 125 | 4LMA001AR/4KLD006CQ-B-01 | U1000R2V | 3G1.5 | 25 | X 041 04 | 1 | 4KLD006CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd floor to HV room |  |  | WCC 14
|  | 126 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 127 | 4LMA001AR/4KLD006CQ-B-02 | U1000R2V | 3G1.5 | 25 | X 041 04 | 3 | 4KLD006CQ | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd floor to HV room |  |  | WCC 14
|  | 128 | [5 empty] | 4
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 98 | 4LMA001AR/4LCA001AR-B-01 | U1000R2V | 3G2.5 | 10 | X 020 04 | 1 | 4LCA001AR | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 1st to 2nd floor | Flue gas |  | WCC 14
|  | 97 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 100 | 4LMA001AR/4LCA001AR-B-02 | U1000R2V | 3G2.5 | 10 | X 020 04 | 5 | 4LCA001AR | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 1st to 2nd floor | Flue gas |  | WCC 14
|  | 99 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 97 | 4LMA001AR/4LCA001BC-B-01 | U1000R2V | 3G2.5 | 58 | X 020 04 | 2 | 4LCA001BC | 400Vca |  |  | Flue gas |  | #N/A
|  | 98 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 99 | 4LMA001AR/4LCA001BC-B-02 | U1000R2V | 3G2.5 | 58 | X 020 04 | 5 | 4LCA001BC | 400Vca |  |  | Flue gas |  | #N/A
|  | 100 | [5 empty] | 6
| PE | PE | [5 empty] | 7
4LMA001AR | X 026 04 | 102 | 4LMA001AR/4LCA002AR-B-01 | U1000R2V | 3G2.5 | 10 | X 020 04 | 1 | 4LCA002AR | 230Vca | ALIMENTATION POUR REDRESSEUR 1 | 2nd floor | Flue gas |  | WCC 14
|  | 101 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 104 | 4LMA001AR/4LCA002AR-B-02 | U1000R2V | 3G2.5 | 10 | X 020 04 | 5 | 4LCA002AR | 230Vca | ALIMENTATION POUR REDRESSEUR 2 | 2nd floor | Flue gas |  | WCC 14
|  | 103 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 101 | 4LMA001AR/4LCA002BC-B-01 | U1000R2V | 3G2.5 | 58 | X 020 04 | 2 | 4LCA002BC | 400Vca |  |  | Flue gas |  | #N/A
|  | 102 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 104 | 4LMA001AR/4LCA002BC-B-02 | U1000R2V | 3G2.5 | 58 | X 020 04 | 5 | 4LCA002BC | 400Vca |  |  | Flue gas |  | #N/A
|  | 103 | [5 empty] | 6
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 25 | 4LMA001AR/4LHA001AR-B-01 | U1000R2V | 3G2.5 | 10 | X 048 03 | 2 | 4LHA001AR | 230Vca |  | 1st to 2nd floor |  |  | WCC 14
|  | 26 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 23 | 4LMA001AR/4LKA001AR-B-01 | U1000R2V | 3G2.5 | 10 | X 084 03 | 2 | 4LKA001AR | 230Vca |  | 1st to 2nd floor | Water steam |  | WCC 14
|  | 24 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 9 | 4LMA001AR/4LKA001AR-B-02 | U1000R2V | 3G2.5 | 10 | X 088 03 | 1 | 4LKA001AR | 48Vca |  | 1st to 2nd floor | Water steam |  | WCC 14
|  | 10 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | XA 034 03 | 1 | 4LMA001AR/4LKD001AR-B-01 | U1000R2V | 3G2.5 | 12 | X 026 04 | 16 | 4LKD001AR | 230Vca |  | 2nd floor | Water steam |  | WCC 14
|  | 2 | [5 empty] | 15
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | XA 035 03 | 1 | 4LMA001AR/4LKD001AR-B-02 | U1000R2V | 3G2.5 | 12 | X 026 04 | 18 | 4LKD001AR | 230Vca |  | 2nd floor | Water steam |  | WCC 14
|  | 2 | [5 empty] | 17
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | XA 036 03 | 1 | 4LMA001AR/4LKD001AR-B-03 | U1000R2V | 3G2.5 | 12 | X 059 03 | 1 | 4LKD001AR | 230Vca |  | 2nd floor | Water steam |  | WCC 14
|  | 2 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | XA 037 03 | 1 | 4LMA001AR/4LKD001AR-B-04 | U1000R2V | 3G2.5 | 12 | X 059 03 | 15 | 4LKD001AR | 230Vca |  | 2nd floor | Water steam |  | WCC 14
|  | 2 | [5 empty] | 16
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 20 | 4LMA001AR/4LKF001AR-B-01 | U1000R2V | 3G2.5 | 12 | XA 034 03 | 1 | 4LKF001AR | 230Vca |  | 2nd floor |  |  | WCC 14
|  | 19 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 22 | 4LMA001AR/4LKF001AR-B-02 | U1000R2V | 3G2.5 | 12 | XA 035 03 | 1 | 4LKF001AR | 230Vca |  | 2nd floor |  |  | WCC 14
|  | 21 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 3 | 4LMA001AR/4LKF001AR-B-03 | U1000R2V | 3G2.5 | 12 | XA 036 03 | 1 | 4LKF001AR | 230Vca |  | 2nd floor |  |  | WCC 14
|  | 4 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 059 03 | 17 | 4LMA001AR/4LKF001AR-B-04 | U1000R2V | 3G2.5 | 12 | XA 037 03 | 1 | 4LKF001AR | 230Vca |  | 2nd floor |  |  | WCC 14
|  | 18 | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 28 | 4LMA001AR/4LKM001AR-B-01 | U1000R2V | 3G2.5 | 10 | X 025 03 | 6 | 4LKM001AR | 230Vca |  | 2nd floor |  |  | WCC 14
|  | 27 | [5 empty] | 12
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 2 | 4LMA001AR/4LKP001AR-B-01 | CR1-C1 | 3G2.5 | 10 | X | ? | 4LKP001AR | 230Vca |  |  |  |  | WCC 14
|  | 1 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 025 04 | 2 | 4LMA001AR/4LMA001CR-B-01 | U1000R2V | 5G16 | 10 | X | ? | 4LMA001CR | 230Vca | ALIMENTATION PRINCIPALE ARMOIRE TABLEAU SOUS DISTRIBUTION ONDULÉE TRAITEMENT DES FUMÉES | 2nd floor |  | PRIO | WCC 22
|  | 3 | [5 empty] | ?
|  | 4 | [5 empty] | ?
|  | 1 | [5 empty] | ? | [6 empty] | #N/A
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 8 | 4LMA001AR/4SAR200BC-B-01 | U1000R2V | 3G2.5 | 10 | X02.01 | 1 | 4SAR200BC | 230Vca |  |  | Pneumatic system |  | WCC 14
|  | 7 | [5 empty] | 3N
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 10 | 4LMA001AR/4SAR400BC-B-01 | U1000R2V | 3G2.5 | 10 | X02.01 | 1 | 4SAR400BC | 230Vca |  |  | Pneumatic system |  | WCC 14
|  | 9 | [5 empty] | 3N
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 70 | 4LMA001AR/4SEO220JQI-B-01 | U1000R2V | 3G1.5 | 10 | X | L | 4SEO220JQI | 230Vca |  |  | Flue gas |  | WCC 14
|  | 69 | [5 empty] | N
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 40 | 4LMA001AR/CAMERA PC-B-01 | U1000R2V | 3G2.5 | 10 | X | ? | CAMERA PC | 230Vca |  |  |  |  | WCC 14
|  | 39 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 09 | 2 | 4LMA001AR/POSTE HTA-B-01 | U1000R2V | 3G4 | 10 | X | ? | POSTE HTA | 230Vca |  | 2nd floot to HV room |  |  | WCC 14
|  | 1 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 09 | 4 | 4LMA001AR/POSTE HTA-B-02 | U1000R2V | 3G4 | 10 | X | ? | POSTE HTA | 230Vca |  | 2nd floot to HV room |  |  | WCC 14
|  | 3 | [5 empty] | ?
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 170 | 4LMA001AR/SALLE CONTROLE-B-01 | U1000R2V | 3G2.5 | 10 | X | 2 | SALLE CONTROLE | 230Vca |  | 2nd to 4th floor |  |  | WCC 14
|  | 169 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001AR | X 026 04 | 172 | 4LMA001AR/SALLE CONTROLE-B-02 | U1000R2V | 3G2.5 | 10 | X | 2 | SALLE CONTROLE | 230Vca |  | 2nd to 4th floor |  |  | WCC 14
|  | 171 | [5 empty] | 1
| PE | PE |  |  |  |  | PE | PE
4LMA001TR |  | L1 | 4LMA001TR/4LKM001AR-B-01 | U1000R2V | 5G70 | 10 | IG 026 04 |  | 4LKM001AR | 400Vca |  | 2nd floor |  | PRIO | WCC 38
|  | L2 | [12 empty] | #N/A
L3
N
| PE | PE |  |  |  |  | PE | PE | [6 empty] | #N/A
4UPS001LD | X50 | L1 | 4UPS001LD/4LMA001AR-B-01 | U1000R2V | 5G70 | 25 | IG 020 04.1 | 4 | 4LMA001AR | 400Vca | UPS 1 400 VCA ARRIVEE DU TABLEAU DE DISTRIBUTION ONDULÉE | 2nd floor |  | PRIO | WCC 38
|  | L2 | [5 empty] | 6
|  | L3 | [5 empty] | 8
|  | N | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4UPS001LD | X 074 04 | 1 | 4UPS001LD/4LMA001AR-C-01 | U1000R2V | 7G1.5 | 10 | X? |  | 4LMA001AR | 24Vcc |  | 2nd floor |  |  | #N/A
2
3
4
| PE | PE |  |  |  |  | PE | PE
4UPS002LD | X50 | L1 | 4UPS002LD/4LMA001AR-B-01 | U1000R2V | 5G70 | 45 | IG 020 09 | 4 | 4LMA001AR | 400Vca | UPS 2 400 VCA ARRIVEE DU TABLEAU DE DISTRIBUTION ONDULÉE | 2nd to 3rd floor |  | PRIO | WCC 38
|  | L2 | [5 empty] | 6
|  | L3 | [5 empty] | 8
|  | N | [5 empty] | 2
| PE | PE |  |  |  |  | PE | PE
4UPS002LD | X 070 04 | 33 | 4UPS002LD/4LMA001AR-C-01 | U1000R2V | 7G1.5 | 10 | X? |  | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor |  |  | #N/A
34
35
36
| PE | PE |  |  |  |  | PE | PE
4UPS002LD | X 074 04 | 37 | 4UPS002LD/4LMA001AR-C-02 | U1000R2V | 12G1.5 | 10 | X? |  | 4LMA001AR | 24Vcc |  | 2nd to 3rd floor |  |  | WCC 18
38
39
|  | 40 | [12 empty] | #N/A
41
42
|  | 43 | [12 empty] | #N/A
44
#N/A
| PE | PE |  |  |  |  | PE | PE
Q02204_S | OUT | + | Q02204_S/Q02304_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02304_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02304_S | OUT | + | Q02304_S/Q02404_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02404_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02404_S | OUT | + | Q02404_S/Q02504_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02504_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02504_S | OUT | + | Q02504_S/Q02604_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02604_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02604_S | OUT | + | Q02604_S/Q02704_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02704_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02704_S | OUT | + | Q02704_S/Q02804_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02804_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02804_S | OUT | + | Q02804_S/Q02904_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q02904_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q02904_S | OUT | + | Q02904_S/Q03004_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q03004_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q03004_S | OUT | + | Q03004_S/Q03104_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q03104_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
Q03104_S | OUT | + | Q03104_S/Q03204_S-C-01 | U1000R2V | 3G1.5 | 5 | IN | + | Q03204_S | 400Vca |  |  | Primary air system |  | WCC 14
|  | - | [5 empty] | -
| PE | PE |  |  |  |  | PE | PE
WP3 | KF 301 03 | -X1 P1 | WP3/4KLD002CQ-S-01 |  |  | 15 |  |  | 4KLD002CQ |  |  |  | Ash system
WP3 | KF 302 03 | -X1 P1 | WP3/4KLD002CQ-S-02 |  |  | 15 |  |  | 4KLD002CQ |  |  |  | Ash system

## Tipovi kabela_Albioma
Type | Formation | Vanjski promjer kabela Tim kabel | Vanjski promjer kabela Miguelez (rematec) | Vanjski promjer kabela Birtas kablos | Vanjski promjer kabela prosječan | Obujmica Rittal | Obujmica Phoenix | Note
01IP09EGSF | 1x2x0.88 |  |  | 7.1 | 7.1 | 1- 7077000 | WCC 14
04IP09EISF | 4x2x0.88 |  |  | 17.6 | 17.6 | 2- 7078000 | WCC 18
08IP09EISF | 8x2x0.88 |  |  | 23.6 | 23.6 | 4- 7097220 | WCC 26
12IP09EISF | 12x2x0.88 |  |  | 28.8 | 28.8 | 5- 7097260 | WCC 30
BIRTFLEX 5111-PVC-PUR-JB | 4G0.75 |  |  | 7.9 | 7.9 | 1- 7077000 | WCC 14
CR1-C1 | 4x25 | 26.3 |  |  | 26.3 | 5- 7097260 | WCC 30 | nije CR1-C1 nego je NHXH FE180/E90
CR1-C1 | 3G2.5 | 12.4 |  |  | 12.4 | 1- 7077000 | WCC 14 | nije CR1-C1 nego je NHXH FE180/E91 i nije 3G2.5 nego je3x2.5
U1000R2V | 3G1.5 |  | 9.5 |  | 9.5 | 1- 7077000 | WCC 14
U1000R2V | 5G6 |  | 15.8 |  | 15.8 | 2- 7078000 | WCC 18
U1000R2V | 5G1.5 |  | 10.7 |  | 10.7 | 1- 7077000 | WCC 14
U1000R2V | 12G1.5 |  | 15.3 |  | 15.3 | 2- 7078000 | WCC 18
U1000R2V | 3G2.5 |  | 10.3 |  | 10.3 | 1- 7077000 | WCC 14
U1000R2V | 27G1.5 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
U1000R2V | 7G1.5 |  | 12 |  | 12 | 1- 7077000 | WCC 14
U1000R2V | 4G2.5 |  | 10.5 |  | 10.5 | 1- 7077000 | WCC 14
U1000R2V | 1x185 | 25.3 | 22.2 |  | 23.75 | 4- 7097220 | WCC 26
U1000R2V | 1x240 | 28.3 | 25.1 |  | 26.7 | 5- 7097260 | WCC 30
U1000R2V | 1x120 | 21 | 18.3 |  | 19.65 | 3- 7097000 | WCC 22
U1000R2V | 1x300 | 30.3 | 29.7 |  | 30 | 5- 7097260 | WCC 30
U1000R2V | 1x150 | 23.3 | 20.4 |  | 21.85 | 3- 7097000 | WCC 22
U1000R2V | 1x95 | 19 | 16.7 |  | 17.85 | 2- 7078000 | WCC 18
U1000R2V | 1x50 | 16 | 12.9 |  | 14.45 | 2- 7078000 | WCC 18
U1000R2V | 4G50 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
U1000R2V | 4G70 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
U1000R2V | 1x70 | 17 | 14.7 |  | 15.85 | 2- 7078000 | WCC 18
U1000R2V | 1x35 | 14 | 11.7 |  | 12.85 | 1- 7077000 | WCC 14
U1000R2V | 4G6 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
U1000R2V | 4G25 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
U1000R2V | 4G4 |  | 12 |  | 12 | 1- 7077000 | WCC 14
U1000R2V | 5G16 |  | 20.3 |  | 20.3 | 3- 7097000 | WCC 22
U1000R2V | 5G2.5 |  | 12.2 |  | 12.2 | 1- 7077000 | WCC 14
U1000R2V | 5G70 |  | 37.1 |  | 37.1 | 7- 7097340 | WCC 38
U1000R2V | 3G4 |  | 11.6 |  | 11.6 | 1- 7077000 | WCC 14
U1000R2V | 3G6 |  | 13 |  | 13 | 1- 7077000 | WCC 14
U1000R2V | 3G10 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2XSLCYK-JB EMV-UV (drugi presjek PE vodića) | 3x120+70 |  |  | 46.5 | 46.5 | 9- 7098100 | WCC 56
2XSLCYK-JB EMV-UV (drugi presjek PE vodića) | 3x70+35 |  |  | 36.9 | 36.9 | 7- 7097340 | WCC 38
2XSLCYK-JB EMV-UV (drugi presjek PE vodića) | 3x50+25 |  |  | 32 | 32 | 6- 7097300 | WCC 34
2XSLCYK-JB EMV-UV (drugi presjek PE vodića) | 3x6+3x1.0 |  |  |  | #DIV/0! | #DIV/0! | #DIV/0!
2XSLCYK-JB EMV-UV (drugi presjek PE vodića) | 3x35+16 |  |  | 27.6 | 27.6 | 5- 7097260 | WCC 30
2XSLCYK-JB EMV-UV | 3x120+3x16
2XSLCYK-JB EMV-UV | 3x70+3x10
2XSLCYK-JB EMV-UV | 3x50+3x10
2XSLCYK-JB EMV-UV | 3x6+3x1.0
2XSLCYK-JB EMV-UV | 3x35/16

## tipovi obujmica
RITTAL obujmica - TIP | RITTAL min Ø | RITTAL max Ø | PHOENIX obujmica - TIP | PHOENIX min Ø | PHOENIX max Ø
1- 7077000 | 6 | 14 | WCC 14 | 6 | 14
2- 7078000 | 12 | 18 | WCC 18 | 12 | 18
3- 7097000 | 18 | 22 | WCC 22 | 18 | 22
4- 7097220 | 22 | 26 | WCC 26 | 22 | 26
5- 7097260 | 26 | 30 | WCC 30 | 26 | 30
6- 7097300 | 30 | 34 | WCC 34 | 30 | 34
7- 7097340 | 34 | 38 | WCC 38 | 34 | 38
8- 7098000 | 38 | 42 | WCC 42 | 38 | 42
9- 7098100 | 42 | 56 | WCC 56 | 42 | 56
10- 7099000 | 56 | 64 | WCC 64 | 56 | 64

## tipovi kabela
Tip kabela - ALBIOMA | Firma | Vanjski promjer [mm2] | plastika nabla | metalna uvodnica RITTAL | plastične uvodnice RITTAL | metalna uvodnica JACOB | plastične uvodnicae JACOB | metalna uvodnica SCHNIDER | Obujmica RITTAL | Obujmica PHOENIX | Namjena | Lokacija | Komentar
ALBIOMA TIPOVI KABELA
2XSL(St)CYK-J 4G120 (3x120/70) | AXINDUS | 45.8 | - | - | - | - | - | - | 7098100 | WCC56 | VFD - MOTORI
2XSL(St)CYK-J 4G70 (3x70/35) | AXINDUS | 36.3 | - | M50 | M50 | M63 | M63 | - | 7097340 | WCC38 | VFD - MOTORI
2XSL(St)CYK-J 4G50 (3x50/25) | AXINDUS | 32.1 | - | M50 | M50 | M50 | M50 | - | 7097300 | WCC34 | VFD - MOTORI
2XSL(St)CYK-J 4G25 (3x25/16) | AXINDUS | 24.4 | M40 | M40 | M40 | M40 | M40 | M40 | 7097220 | WCC26 | VFD - MOTORI
2XSL(St)CYK-J 4G6 (3x6/6) | AXINDUS | 15.6 | M25 | M25 | M25 | M25 | M25 | M25 | 7078000 | WCC18 | VFD - MOTORI
|  |  | - | - | - | - | - | - | - | -
U1000R2V 4x2,5 | Rematec (podaci Miguelez) | 11.1 | M20 | M20 | M20 | M20 | M20 | M20 | 7077000 | WCC14 | napajanje
U1000R2V 4x4 | Rematec (podaci Miguelez) | 12.3 | M20 | M25 | M25 | M20 | M20 | M25 | 7077000 | WCC14 | napajanje
U1000R2V 4x16 | Rematec (podaci Miguelez) | 18.4 | - | - | - | - | - | - | 7097000 | WCC22 | napajanje
U1000R2V 4x25 | Rematec (podaci Miguelez) | 22.8 | M40 | M40 | M40 | M40 | M40 | M40 | 7097220 | WCC26 | napajanje
U1000R2V 5x2,5 | Rematec (podaci Tim kabel) | 15 | M25 | M25 | M25 | M25 | M25 | M25 | 7078000 | WCC18 | napajanje
U1000R2V 5G2.5 mm² | Rematec (podaci Miguelez) | 12.2 | M20 | M25 | M25 | M20 | M20 | M25 | 7077000 | WCC14 | napajanje
U1000R2V 5G1.5 mm² | Rematec (podaci Miguelez) | 10.7 | M20 | M20 | M20 | M20 | M20 | M20 | 7077000 | WCC14 | napajanje
U1000R2V 4x2.5 mm² | Rematec (podaci Miguelez) | 11.1 | M20 | M20 | M20 | M20 | M20 | M20 | 7077000 | WCC14 | napajanje
U1000R2V 4G2.5 mm² |  | 10.5 | M20 | M20 | M20 | M20 | M20 | M20 | 7077000 | WCC14 | napajanje |  | U SHEMI - NE POSTOJI 4G2,5mm2 kabel
U1000R2V 3G2.5 mm² | Rematec (podaci Miguelez) | 10.3 | M20 | M20 | M20 | M20 | M20 | M20 | 7077000 | WCC14 | napajanje
U1000R2V 3G1.5 mm² | Rematec (podaci Miguelez) | 9.5 | M16 | M16 | M16 | M20 | M20 | M16 | 7077000 | WCC14
|  |  | - | - | - | - | - | - | - | -
U1000R2V 27x1.5 mm² | Miguelez cables | 22.5 | M40 | M40 | M40 | M40 | M40 | M40 | 7097220 | WCC26 | Signalni kabel DI/DO | -> JB | BARRYNAX U1000R2V (30G1,5 podatak uzet)
U1000R2V 12x1.5 mm² | Miguelez cables | 14.8 | M25 | M25 | M25 | M25 | M25 | M25 | 7078000 | WCC18 | Signalni kabel DI/DO | -> JB
U1000R2V 8x1.5 mm² | Miguelez cables | 13.5 | M25 | M25 | M25 | M25 | M25 | M25 | 7077000 | WCC14 | Signalni kabel DI/DO | -> JB
BIRTFLEX 5111-PVC-PUR - 4G0,75 | Birtas kablos | 7.9 | M16 | M16 | M16 | - | - | M16 | 7077000 | WCC14 | senzori DI/DO | JB -> senzor
FABER 100 P 4G0,75 |  | 6.2 | M16 | M16 | M16 | - | M12 | M16 | 7077000 | WCC14 | senzori DI/DO | JB -> senzor
FABER THERM 145-MC 04G0,75 |  | 7 | M16 | M16 | M16 | - | M12 | M16 | 7077000 | WCC14 | senzori DI/DO | JB -> senzor
|  |  | - | - | - | - | - | - | - | -
EGSF - CU - 12x2x0,75 | Birtas kablos | 17.1 | - | - | - | - | - | - | 7078000 | WCC18 | Signalni kabel AI/AO | -> JB | prije bio (RE-2Y(St)Y-fl)
EGSF - CU - 8x2x0,75 | Birtas kablos | 14 | M25 | M25 | M25 | M25 | M25 | M25 | 7077000 | WCC14 | Signalni kabel AI/AO | -> JB | prije bio (RE-2Y(St)Y-fl)
EGSF - CU - 4x2x0,75 |  |  | - | - | - | - | - | - | - | - | Signalni kabel AI/AO | -> JB | prije bio (RE-2Y(St)Y-fl)
EISF - CU - 1x2x0,5 | Birtas kablos | 6 | M16 | M16 | M16 | M12 | M12 | M16 | 7077000 | WCC14 | senzori AI/AO | JB -> senzor | prije bio (RE-2Y(St)Y-fl)
|  |  | - | - | - | - | - | - | - | -
|  |  | - | - | - | - | - | - | - | -
12IP09EISF BU 12x2x0.75 mm² | Birtas kablos | 26.6 | M40 | M40 | M40 | M40 | M40 | M40 | 7097260 | WCC30 |  |  | U SHEMI
08IP09EISF BU 8x2x0.75 mm² | Birtas kablos | 22.5 | M40 | M40 | M40 | M40 | M40 | M40 | 7097220 | WCC26 |  |  | U SHEMI
04IP09EISF BU 4x2x0.75 mm² | Birtas kablos | 16.9 | M25 | M25 | M25 | - | M25 | M25 | 7078000 | WCC18 |  |  | U SHEMI
01IP09EISF BU 1x2x0.88 mm² | Sab cables | 13.5 | M25 | M25 | M25 | M25 | M25 | M25 | 7077000 | WCC14 |  |  | U SHEMI
FABER 100 P 4x0.75 mm² |  | 6.2 | M16 | M16 | M16 | - | M12 | M16 | 7077000 | WCC14 |  |  | U SHEMI - NE POSTOJI TAKAV FABER (BEZ G)
NOTE |  |  | UKLJUČEN M16 | UKLJUČEN M16 | UKLJUČEN M16
MONTSINERY TIPOVI KABELA
BARRYNAX U-1000 R2V 5G2,5 |  | 11.5 | M16 ili M20 | M16 ili M20
BARRYNAX U-1000 R2V 4G2,5 |  | 10.5 | M16 ili M20 | M16 ili M20
BARRYNAX U-1000 R2V 3G2,5 |  | 10 | M16 ili M20 | M16 ili M20
BARRYNAX U-1000 R2V 3G1,5 |  | 9.2 | M16 ili M20 | M16 ili M20
BARRYNAX U-1000 R2V 27G1,5 (30G1,5 uzeo) |  | 22.5 | M40 | M40
BARRYNAX U-1000 R2V 12G1,5 |  | 14.8 | M25 | M25
BARRYNAX U-1000 R2V 1X95 |  | 16.2 | M25 ili M32 | M25 ili M32
BARRYNAX U-1000 R2V 1X35 |  | 11.5 | M20 ili M25 | M20 ili M25
BARRYNAX U-1000 R2V 1X16 |  | 8.8 | M16 ili M20 | M16 ili M20
CCL
RE-2Y(St)Yv-fl 12X2X0,75 |  | 15.7 | M25 | M25 | [6 empty] | odabrat min uvodnicu
RE-2Y(St)Yv-fl 08X2X0,75 |  | 13.1 | M25 | M25 | [6 empty] | odabrat min uvodnicu
RE-2Y(St)Yv-fl 04X2X0,75 |  | 9.6 | M16 ili M20 | M16 ili M20 | [6 empty] | odabrat min uvodnicu
RE-2Y(St)Y-fl 01X2X0,5 |  | 5.6 | M12 ili M16 | M12 ili M16 | [6 empty] | odabrat min uvodnicu | Do senzora | Do senzora
FABER 100 P 4G0,75 |  | 6.2 | M12 ili M16 | M12 ili M16 | [6 empty] | odabrat min uvodnicu | Do senzora | Do senzora
FABER THERM 145-MC 04G0,75 |  | 7 | M16 ili M20 | M16 ili M20 | [6 empty] | odabrat min uvodnicu | Do senzora (heat) | Do senzora (heat)
BARRYFLEX H07V-K 1X6 G/Y
NYCWY 03X185/95 |  | 50 | M72 | M72
NAYCY 03X120/95 |  | 46,3(+-3mm) | M72 | M72
NYCWY 03X95/50 |  | 37.8 | M63 | M63
BARRYNAX U-1000 R2V 3X70+1X50 |  | 33.6 | M50 | M50
BARRYNAX U-1000 R2V 3X50+1X35 |  | 28.6 | M50 | M50
BARRYNAX U-1000 R2V 4G35 |  | 25.4 | M40 | M40
BARRYNAX U-1000 R2V 4G16 |  | 18.4 | M32 | M32
NYCWY 03X16/16 |  | 21.4 | M40 | M40
EMV 2XSL(St)CHv-JB 04X10 0,6/1 kV
BARRYNAX U-1000 R2V 4G10 |  | 16.3
BARRYNAX U-1000 R2V 5G6 |  | 15.7 | M25 | M25
EMV 2XSL(St)CHv-JB 04X4 0,6/1 kV
NYCY 03X2,5/2,5 |  | 14.2 | M25 | M25
Note on D23: Luka Božićević: Miguelez nema taj tip kabela
Note on D33: Luka Božićević: EGSF 1x2x0,5

## Obujmice-trolist
KABELI | [18 empty] | TROLIST
Tip kabela | Promjer kabela | Promjer kabela u trolistu | 1- 7077000 | 2- 7078000 | 3- 7097000 | 4- 7097220 | 5- 7097260 | 6- 7097300 | 7- 7097340 | 8- 7098000 | 9- 7098100 | 10- 7099000 | [6 empty] | Tip kabela | Promjer kabela | Promjer kabela u trolistu | 1- 7077000 | 2- 7078000 | 3- 7097000 | 4- 7097220 | 5- 7097260 | 6- 7097300 | 7- 7097340 | 8- 7098000 | 9- 7098100 | 10- 7099000
NA2XS(F)2Y 1x120/16 mm² 20,8/36kV | 44 | 94.82 | 0.31818 | 0.40909 | 0.5 | 0.59091 | 0.68182 | 0.77273 | 0.86364 | 0.95455 | 1.2727 | 1.4545 |  | Ne stane kabel |  |  |  |  | NA2XS(F)2Y 1x120/16 mm² 20,8/36kV | 44 | 94.82 | 0.14765 | 0.18983 | 0.23202 | 0.2742 | 0.31639 | 0.35857 | 0.40076 | 0.44294 | 0.59059 | 0.67496
N2XS(F)2Y 1x70/16 mm² 20,8/36kV | 40.5 | 87.2775 | 0.34568 | 0.44444 | 0.54321 | 0.64198 | 0.74074 | 0.83951 | 0.93827 | 1.037 | 1.3827 | 1.5802 |  | Stane 1 kabel |  |  |  |  | N2XS(F)2Y 1x70/16 mm² 20,8/36kV | 40.5 | 87.2775 | 0.16041 | 0.20624 | 0.25207 | 0.2979 | 0.34373 | 0.38956 | 0.43539 | 0.48122 | 0.64163 | 0.73329
NA2XS(F)2Y 1x240/25 mm² 6/10kV | 39 | 84.045 | 0.35897 | 0.46154 | 0.5641 | 0.66667 | 0.76923 | 0.87179 | 0.97436 | 1.0769 | 1.4359 | 1.641 |  | Stanu 2 kabela |  |  |  |  | NA2XS(F)2Y 1x240/25 mm² 6/10kV | 39 | 84.045 | 0.16658 | 0.21417 | 0.26176 | 0.30936 | 0.35695 | 0.40455 | 0.45214 | 0.49973 | 0.66631 | 0.7615
N2XS(F)2Y 1x150/25 mm² 6/10kV | 35 | 75.425 | 0.4 | 0.51429 | 0.62857 | 0.74286 | 0.85714 | 0.97143 | 1.0857 | 1.2 | 1.6 | 1.8286 |  | Stane trolist |  |  |  |  | N2XS(F)2Y 1x150/25 mm² 6/10kV | 35 | 75.425 | 0.18561 | 0.23865 | 0.29168 | 0.34471 | 0.39775 | 0.45078 | 0.50381 | 0.55684 | 0.74246 | 0.84853
NYY-J 4x70 mm² | 40 | 86.2 | 0.35 | 0.45 | 0.55 | 0.65 | 0.75 | 0.85 | 0.95 | 1.05 | 1.4 | 1.6 |  | Stane 4 kabela |  |  |  |  | NYY-J 4x70 mm² | 40 | 86.2 | 0.16241 | 0.20882 | 0.25522 | 0.30162 | 0.34803 | 0.39443 | 0.44084 | 0.48724 | 0.64965 | 0.74246
NAYY 1x120 mm² | 22 | 47.41 | 0.63636 | 0.81818 | 1 | 1.1818 | 1.3636 | 1.5455 | 1.7273 | 1.9091 | 2.5455 | 2.9091 | [6 empty] | NAYY 1x120 mm² | 22 | 47.41 | 0.2953 | 0.37967 | 0.46404 | 0.54841 | 0.63278 | 0.71715 | 0.80152 | 0.88589 | 1.1812 | 1.3499
NYY-J 1x95 mm² | 21 | 45.255 | 0.66667 | 0.85714 | 1.0476 | 1.2381 | 1.4286 | 1.619 | 1.8095 | 2 | 2.6667 | 3.0476 | [6 empty] | NYY-J 1x95 mm² | 21 | 45.255 | 0.30936 | 0.39775 | 0.48613 | 0.57452 | 0.66291 | 0.7513 | 0.83969 | 0.92807 | 1.2374 | 1.4142
NYY-J 1x35 mm² | 16 | 34.48 | 0.875 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125 | 2.375 | 2.625 | 3.5 | 4 |  | Obujmica | min | max | avg | gleda | NYY-J 1x35 mm² | 16 | 34.48 | 0.40603 | 0.52204 | 0.63805 | 0.75406 | 0.87007 | 0.98608 | 1.1021 | 1.2181 | 1.6241 | 1.8561
NYY-J 5x16 mm² | 25 | 53.875 | 0.56 | 0.72 | 0.88 | 1.04 | 1.2 | 1.36 | 1.52 | 1.68 | 2.24 | 2.56 |  | 1- 7077000 | 6 | 14 | 10 | 14 | NYY-J 5x16 mm² | 25 | 53.875 | 0.25986 | 0.33411 | 0.40835 | 0.4826 | 0.55684 | 0.63109 | 0.70534 | 0.77958 | 1.0394 | 1.1879
NYY-J 1x16 mm² | 13 | 28.015 | 1.0769 | 1.3846 | 1.6923 | 2 | 2.3077 | 2.6154 | 2.9231 | 3.2308 | 4.3077 | 4.9231 |  | 2- 7078000 | 12 | 18 | 15 | 18 | NYY-J 1x16 mm² | 13 | 28.015 | 0.49973 | 0.64251 | 0.78529 | 0.92807 | 1.0709 | 1.2136 | 1.3564 | 1.4992 | 1.9989 | 2.2845
NYY-J 4x4 mm² | 19 | 40.945 | 0.73684 | 0.94737 | 1.1579 | 1.3684 | 1.5789 | 1.7895 | 2 | 2.2105 | 2.9474 | 3.3684 |  | 3- 7097000 | 18 | 22 | 20 | 22 | NYY-J 4x4 mm² | 19 | 40.945 | 0.34192 | 0.43961 | 0.53731 | 0.635 | 0.73269 | 0.83038 | 0.92807 | 1.0258 | 1.3677 | 1.5631
NYY-J 3x4 mm² | 17 | 36.635 | 0.82353 | 1.0588 | 1.2941 | 1.5294 | 1.7647 | 2 | 2.2353 | 2.4706 | 3.2941 | 3.7647 |  | 4- 7097220 | 22 | 26 | 24 | 26 | NYY-J 3x4 mm² | 17 | 36.635 | 0.38215 | 0.49133 | 0.60052 | 0.7097 | 0.81889 | 0.92807 | 1.0373 | 1.1464 | 1.5286 | 1.747
NYY-J 4x2,5 mm² | 17 | 36.635 | 0.82353 | 1.0588 | 1.2941 | 1.5294 | 1.7647 | 2 | 2.2353 | 2.4706 | 3.2941 | 3.7647 |  | 5- 7097260 | 26 | 30 | 28 | 30 | NYY-J 4x2,5 mm² | 17 | 36.635 | 0.38215 | 0.49133 | 0.60052 | 0.7097 | 0.81889 | 0.92807 | 1.0373 | 1.1464 | 1.5286 | 1.747
NYY-J 3x2,5 mm² | 15 | 32.325 | 0.93333 | 1.2 | 1.4667 | 1.7333 | 2 | 2.2667 | 2.5333 | 2.8 | 3.7333 | 4.2667 |  | 6- 7097300 | 30 | 34 | 32 | 34 | NYY-J 3x2,5 mm² | 15 | 32.325 | 0.4331 | 0.55684 | 0.68059 | 0.80433 | 0.92807 | 1.0518 | 1.1756 | 1.2993 | 1.7324 | 1.9799
YSLY-JZ 12x1,5 mm² | 12.4 | 26.722 | 1.129 | 1.4516 | 1.7742 | 2.0968 | 2.4194 | 2.7419 | 3.0645 | 3.3871 | 4.5161 | 5.1613 |  | 7- 7097340 | 34 | 38 | 36 | 38 | YSLY-JZ 12x1,5 mm² | 12.4 | 26.722 | 0.52391 | 0.6736 | 0.82329 | 0.97298 | 1.1227 | 1.2724 | 1.422 | 1.5717 | 2.0957 | 2.395
YSLY-JZ 5x1,5 mm² | 8.2 | 17.671 | 1.7073 | 2.1951 | 2.6829 | 3.1707 | 3.6585 | 4.1463 | 4.6341 | 5.122 | 6.8293 | 7.8049 |  | 8- 7098000 | 38 | 42 | 40 | 42 | YSLY-JZ 5x1,5 mm² | 8.2 | 17.671 | 0.79226 | 1.0186 | 1.245 | 1.4713 | 1.6977 | 1.9241 | 2.1504 | 2.3768 | 3.169 | 3.6218
YSLCY-JZ 12x0,75 mm² | 10.7 | 23.0585 | 1.3084 | 1.6822 | 2.0561 | 2.4299 | 2.8037 | 3.1776 | 3.5514 | 3.9252 | 5.2336 | 5.9813 |  | 9- 7098100 | 42 | 56 | 49 | 56 | YSLCY-JZ 12x0,75 mm² | 10.7 | 23.0585 | 0.60715 | 0.78062 | 0.9541 | 1.1276 | 1.301 | 1.4745 | 1.648 | 1.8215 | 2.4286 | 2.7755
LiYCY 4x0,75 mm² | 7.6 | 16.378 | 1.8421 | 2.3684 | 2.8947 | 3.4211 | 3.9474 | 4.4737 | 5 | 5.5263 | 7.3684 | 8.4211 |  | 10- 7099000 | 56 | 64 | 60 | 64 | LiYCY 4x0,75 mm² | 7.6 | 16.378 | 0.85481 | 1.099 | 1.3433 | 1.5875 | 1.8317 | 2.076 | 2.3202 | 2.5644 | 3.4192 | 3.9077
RE-2Y(St)Yv 2x2x0,75 mm² | 8.8 | 18.964 | 1.5909 | 2.0455 | 2.5 | 2.9545 | 3.4091 | 3.8636 | 4.3182 | 4.7727 | 6.3636 | 7.2727 | [6 empty] | RE-2Y(St)Yv 2x2x0,75 mm² | 8.8 | 18.964 | 0.73824 | 0.94917 | 1.1601 | 1.371 | 1.5819 | 1.7929 | 2.0038 | 2.2147 | 2.953 | 3.3748
ETHERLINE Y CAT5 2X2XAWG22 | 1.1 | 2.3705 | 12.7273 | 16.3636 | 20 | 23.6364 | 27.2727 | 30.9091 | 34.5455 | 38.1818 | 50.9091 | 58.1818 | [6 empty] | ETHERLINE Y CAT5 2X2XAWG22 | 1.1 | 2.3705 | 5.9059 | 7.5933 | 9.2807 | 10.9682 | 12.6556 | 14.343 | 16.0304 | 17.7178 | 23.6237 | 26.9985
NA2XS(F)2Y 1x95/16mm² 12/20kV (Faber) | 32 | 68.96 | 0.4375 | 0.5625 | 0.6875 | 0.8125 | 0.9375 | 1.0625 | 1.1875 | 1.3125 | 1.75 | 2 | [6 empty] | NA2XS(F)2Y 1x95/16mm² 12/20kV (Faber) | 32 | 68.96 | 0.20302 | 0.26102 | 0.31903 | 0.37703 | 0.43503 | 0.49304 | 0.55104 | 0.60905 | 0.81206 | 0.92807
N2XH-O 1x95 mm² (Faber) | 17.9 | 38.5745 | 0.78212 | 1.0056 | 1.2291 | 1.4525 | 1.676 | 1.8994 | 2.1229 | 2.3464 | 3.1285 | 3.5754 | [6 empty] | N2XH-O 1x95 mm² (Faber) | 17.9 | 38.5745 | 0.36293 | 0.46663 | 0.57032 | 0.67402 | 0.77772 | 0.88141 | 0.98511 | 1.0888 | 1.4517 | 1.6591
N2XH-O 1x185 mm² (Faber) | 23.5 | 50.6425 | 0.59574 | 0.76596 | 0.93617 | 1.1064 | 1.2766 | 1.4468 | 1.617 | 1.7872 | 2.383 | 2.7234 | [6 empty] | N2XH-O 1x185 mm² (Faber) | 23.5 | 50.6425 | 0.27645 | 0.35543 | 0.43442 | 0.5134 | 0.59239 | 0.67137 | 0.75036 | 0.82934 | 1.1058 | 1.2638
N2XH-J 4x70 mm² (Faber) | 35 | 75.425 | 0.4 | 0.51429 | 0.62857 | 0.74286 | 0.85714 | 0.97143 | 1.0857 | 1.2 | 1.6 | 1.8286 | [6 empty] | N2XH-J 4x70 mm² (Faber) | 35 | 75.425 | 0.18561 | 0.23865 | 0.29168 | 0.34471 | 0.39775 | 0.45078 | 0.50381 | 0.55684 | 0.74246 | 0.84853
N2XH 1x16mm² (Faber) | 9 | 19.395 | 1.5556 | 2 | 2.4444 | 2.8889 | 3.3333 | 3.7778 | 4.2222 | 4.6667 | 6.2222 | 7.1111 | [6 empty] | N2XH 1x16mm² (Faber) | 9 | 19.395 | 0.72184 | 0.92807 | 1.1343 | 1.3406 | 1.5468 | 1.753 | 1.9593 | 2.1655 | 2.8873 | 3.2998
N2XH-J 4x6 mm² (Faber) | 16 | 34.48 | 0.875 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125 | 2.375 | 2.625 | 3.5 | 4 | [6 empty] | N2XH-J 4x6 mm² (Faber) | 16 | 34.48 | 0.40603 | 0.52204 | 0.63805 | 0.75406 | 0.87007 | 0.98608 | 1.1021 | 1.2181 | 1.6241 | 1.8561
N2XH-J 5x4 mm² (Faber) | 14 | 30.17 | 1 | 1.2857 | 1.5714 | 1.8571 | 2.1429 | 2.4286 | 2.7143 | 3 | 4 | 4.5714 | [6 empty] | N2XH-J 5x4 mm² (Faber) | 14 | 30.17 | 0.46404 | 0.59662 | 0.7292 | 0.86178 | 0.99437 | 1.1269 | 1.2595 | 1.3921 | 1.8561 | 2.1213
N2XH-J 3x4 mm² (Faber) | 14 | 30.17 | 1 | 1.2857 | 1.5714 | 1.8571 | 2.1429 | 2.4286 | 2.7143 | 3 | 4 | 4.5714 | [6 empty] | N2XH-J 3x4 mm² (Faber) | 14 | 30.17 | 0.46404 | 0.59662 | 0.7292 | 0.86178 | 0.99437 | 1.1269 | 1.2595 | 1.3921 | 1.8561 | 2.1213
N2XH-J 4x2,5 mm² (Faber) | 11.5 | 24.7825 | 1.2174 | 1.5652 | 1.913 | 2.2609 | 2.6087 | 2.9565 | 3.3043 | 3.6522 | 4.8696 | 5.5652 | [6 empty] | N2XH-J 4x2,5 mm² (Faber) | 11.5 | 24.7825 | 0.56491 | 0.72632 | 0.88772 | 1.0491 | 1.2105 | 1.3719 | 1.5333 | 1.6947 | 2.2597 | 2.5825
N2XH-J 3x2,5 mm² (Faber) | 11 | 23.705 | 1.2727 | 1.6364 | 2 | 2.3636 | 2.7273 | 3.0909 | 3.4545 | 3.8182 | 5.0909 | 5.8182 | [6 empty] | N2XH-J 3x2,5 mm² (Faber) | 11 | 23.705 | 0.59059 | 0.75933 | 0.92807 | 1.0968 | 1.2656 | 1.4343 | 1.603 | 1.7718 | 2.3624 | 2.6999
HSLH-JZ 12x1,5 mm² (Faber) | 13.2 | 28.446 | 1.0606 | 1.3636 | 1.6667 | 1.9697 | 2.2727 | 2.5758 | 2.8788 | 3.1818 | 4.2424 | 4.8485 | [6 empty] | HSLH-JZ 12x1,5 mm² (Faber) | 13.2 | 28.446 | 0.49216 | 0.63278 | 0.7734 | 0.91401 | 1.0546 | 1.1952 | 1.3359 | 1.4765 | 1.9686 | 2.2499
HSLH-JZ 5x1,5 mm² (Faber) | 8.9 | 19.1795 | 1.573 | 2.0225 | 2.4719 | 2.9213 | 3.3708 | 3.8202 | 4.2697 | 4.7191 | 6.2921 | 7.191 | [6 empty] | HSLH-JZ 5x1,5 mm² (Faber) | 8.9 | 19.1795 | 0.72995 | 0.9385 | 1.1471 | 1.3556 | 1.5642 | 1.7727 | 1.9813 | 2.1898 | 2.9198 | 3.3369
HSLCH-JZ 3x2,5 mm² (Faber) | 9.3 | 20.0415 | 1.5054 | 1.9355 | 2.3656 | 2.7957 | 3.2258 | 3.6559 | 4.086 | 4.5161 | 6.0215 | 6.8817 | [6 empty] | HSLCH-JZ 3x2,5 mm² (Faber) | 9.3 | 20.0415 | 0.69855 | 0.89814 | 1.0977 | 1.2973 | 1.4969 | 1.6965 | 1.8961 | 2.0957 | 2.7942 | 3.1934
HSLCH-JZ 4x0,75 mm² (Faber) | 7.5 | 16.1625 | 1.8667 | 2.4 | 2.9333 | 3.4667 | 4 | 4.5333 | 5.0667 | 5.6 | 7.4667 | 8.5333 | [6 empty] | HSLCH-JZ 4x0,75 mm² (Faber) | 7.5 | 16.1625 | 0.8662 | 1.1137 | 1.3612 | 1.6087 | 1.8561 | 2.1036 | 2.3511 | 2.5986 | 3.4648 | 3.9598
HSLCH-JZ 12x0,75 mm² (Faber) | 11.3 | 24.3515 | 1.2389 | 1.5929 | 1.9469 | 2.3009 | 2.6549 | 3.0088 | 3.3628 | 3.7168 | 4.9558 | 5.6637 | [6 empty] | HSLCH-JZ 12x0,75 mm² (Faber) | 11.3 | 24.3515 | 0.57491 | 0.73917 | 0.90344 | 1.0677 | 1.232 | 1.3962 | 1.5605 | 1.7247 | 2.2997 | 2.6282
NA2XS(F)2Y 1x95/16mm² 12/20kV (TimKabel) | 33.5 | 72.1925 | 0.41791 | 0.53731 | 0.65672 | 0.77612 | 0.89552 | 1.0149 | 1.1343 | 1.2537 | 1.6716 | 1.9104 | [6 empty] | NA2XS(F)2Y 1x95/16mm² 12/20kV (TimKabel) | 33.5 | 72.1925 | 0.19393 | 0.24933 | 0.30474 | 0.36015 | 0.41556 | 0.47096 | 0.52637 | 0.58178 | 0.7757 | 0.88652
NA2XH 1x300mm² (ELAND cables) | 26.7 | 57.5385 | 0.52434 | 0.67416 | 0.82397 | 0.97378 | 1.1236 | 1.2734 | 1.4232 | 1.573 | 2.0974 | 2.397 | [6 empty] | NA2XH 1x300mm² (ELAND cables) | 26.7 | 57.5385 | 0.24332 | 0.31283 | 0.38235 | 0.45187 | 0.52139 | 0.59091 | 0.66043 | 0.72995 | 0.97326 | 1.1123
NA2XH-O 1x150 mm² (ELAND cables) | 19.6 | 42.238 | 0.71429 | 0.91837 | 1.1224 | 1.3265 | 1.5306 | 1.7347 | 1.9388 | 2.1429 | 2.8571 | 3.2653 | [6 empty] | NA2XH-O 1x150 mm² (ELAND cables) | 19.6 | 42.238 | 0.33146 | 0.42616 | 0.52086 | 0.61556 | 0.71026 | 0.80496 | 0.89966 | 0.99437 | 1.3258 | 1.5152
N2XH-J 4x70 mm² (TimKabel) | 35 | 75.425 | 0.4 | 0.51429 | 0.62857 | 0.74286 | 0.85714 | 0.97143 | 1.0857 | 1.2 | 1.6 | 1.8286 | [6 empty] | N2XH-J 4x70 mm² (TimKabel) | 35 | 75.425 | 0.18561 | 0.23865 | 0.29168 | 0.34471 | 0.39775 | 0.45078 | 0.50381 | 0.55684 | 0.74246 | 0.84853
N2XH 1x16mm² (TimKabel) | 9.1 | 19.6105 | 1.5385 | 1.978 | 2.4176 | 2.8571 | 3.2967 | 3.7363 | 4.1758 | 4.6154 | 6.1538 | 7.033 | [6 empty] | N2XH 1x16mm² (TimKabel) | 9.1 | 19.6105 | 0.7139 | 0.91788 | 1.1218 | 1.3258 | 1.5298 | 1.7338 | 1.9377 | 2.1417 | 2.8556 | 3.2636
N2XH-J 1x95 mm² (TimKabel) | 17 | 36.635 | 0.82353 | 1.0588 | 1.2941 | 1.5294 | 1.7647 | 2 | 2.2353 | 2.4706 | 3.2941 | 3.7647 | [6 empty] | N2XH-J 1x95 mm² (TimKabel) | 17 | 36.635 | 0.38215 | 0.49133 | 0.60052 | 0.7097 | 0.81889 | 0.92807 | 1.0373 | 1.1464 | 1.5286 | 1.747
N2XH-J 4x6 mm² (TimKabel) | 14 | 30.17 | 1 | 1.2857 | 1.5714 | 1.8571 | 2.1429 | 2.4286 | 2.7143 | 3 | 4 | 4.5714 | [6 empty] | N2XH-J 4x6 mm² (TimKabel) | 14 | 30.17 | 0.46404 | 0.59662 | 0.7292 | 0.86178 | 0.99437 | 1.1269 | 1.2595 | 1.3921 | 1.8561 | 2.1213
N2XH-J 4x4 mm² (TimKabel) | 12 | 25.86 | 1.1667 | 1.5 | 1.8333 | 2.1667 | 2.5 | 2.8333 | 3.1667 | 3.5 | 4.6667 | 5.3333 | [6 empty] | N2XH-J 4x4 mm² (TimKabel) | 12 | 25.86 | 0.54138 | 0.69606 | 0.85073 | 1.0054 | 1.1601 | 1.3148 | 1.4695 | 1.6241 | 2.1655 | 2.4749
N2XH-J 4x2,5 mm² (TimKabel) | 11 | 23.705 | 1.2727 | 1.6364 | 2 | 2.3636 | 2.7273 | 3.0909 | 3.4545 | 3.8182 | 5.0909 | 5.8182 | [6 empty] | N2XH-J 4x2,5 mm² (TimKabel) | 11 | 23.705 | 0.59059 | 0.75933 | 0.92807 | 1.0968 | 1.2656 | 1.4343 | 1.603 | 1.7718 | 2.3624 | 2.6999
N2XH-J 3x4 mm² (TimKabel) | 11 | 23.705 | 1.2727 | 1.6364 | 2 | 2.3636 | 2.7273 | 3.0909 | 3.4545 | 3.8182 | 5.0909 | 5.8182 | [6 empty] | N2XH-J 3x4 mm² (TimKabel) | 11 | 23.705 | 0.59059 | 0.75933 | 0.92807 | 1.0968 | 1.2656 | 1.4343 | 1.603 | 1.7718 | 2.3624 | 2.6999
N2XH-J 3x2,5 mm² (TimKabel) | 10 | 21.55 | 1.4 | 1.8 | 2.2 | 2.6 | 3 | 3.4 | 3.8 | 4.2 | 5.6 | 6.4 | [6 empty] | N2XH-J 3x2,5 mm² (TimKabel) | 10 | 21.55 | 0.64965 | 0.83527 | 1.0209 | 1.2065 | 1.3921 | 1.5777 | 1.7633 | 1.949 | 2.5986 | 2.9698
HSLH-JZ 5x1,5 mm² (TimKabel) | 8.9 | 19.1795 | 1.573 | 2.0225 | 2.4719 | 2.9213 | 3.3708 | 3.8202 | 4.2697 | 4.7191 | 6.2921 | 7.191 | [6 empty] | HSLH-JZ 5x1,5 mm² (TimKabel) | 8.9 | 19.1795 | 0.72995 | 0.9385 | 1.1471 | 1.3556 | 1.5642 | 1.7727 | 1.9813 | 2.1898 | 2.9198 | 3.3369
HSLH-JZ 12x1,5 mm² (TimKabel) | 13.2 | 28.446 | 1.0606 | 1.3636 | 1.6667 | 1.9697 | 2.2727 | 2.5758 | 2.8788 | 3.1818 | 4.2424 | 4.8485 | [6 empty] | HSLH-JZ 12x1,5 mm² (TimKabel) | 13.2 | 28.446 | 0.49216 | 0.63278 | 0.7734 | 0.91401 | 1.0546 | 1.1952 | 1.3359 | 1.4765 | 1.9686 | 2.2499
HSLCH-JZ 4x0,75 mm² (TimKabel) | 8 | 17.24 | 1.75 | 2.25 | 2.75 | 3.25 | 3.75 | 4.25 | 4.75 | 5.25 | 7 | 8 | [6 empty] | HSLCH-JZ 4x0,75 mm² (TimKabel) | 8 | 17.24 | 0.81206 | 1.0441 | 1.2761 | 1.5081 | 1.7401 | 1.9722 | 2.2042 | 2.4362 | 3.2483 | 3.7123
HSLCH-JZ 12x0,75 mm² (TimKabel) | 11.3 | 24.3515 | 1.2389 | 1.5929 | 1.9469 | 2.3009 | 2.6549 | 3.0088 | 3.3628 | 3.7168 | 4.9558 | 5.6637 | [6 empty] | HSLCH-JZ 12x0,75 mm² (TimKabel) | 11.3 | 24.3515 | 0.57491 | 0.73917 | 0.90344 | 1.0677 | 1.232 | 1.3962 | 1.5605 | 1.7247 | 2.2997 | 2.6282
NA2XH-O 1x185 mm² (ELAND cables) | 21.8 | 46.979 | 0.6422 | 0.82569 | 1.0092 | 1.1927 | 1.3761 | 1.5596 | 1.7431 | 1.9266 | 2.5688 | 2.9358 | [6 empty] | NA2XH-O 1x185 mm² (ELAND cables) | 21.8 | 46.979 | 0.29801 | 0.38315 | 0.46829 | 0.55344 | 0.63858 | 0.72373 | 0.80887 | 0.89402 | 1.192 | 1.3623
NA2XH-O 1x95 mm² (ELAND cables) | 16.1 | 34.6955 | 0.86957 | 1.118 | 1.3665 | 1.6149 | 1.8634 | 2.1118 | 2.3602 | 2.6087 | 3.4783 | 3.9752 | [6 empty] | NA2XH-O 1x95 mm² (ELAND cables) | 16.1 | 34.6955 | 0.40351 | 0.5188 | 0.63409 | 0.74938 | 0.86467 | 0.97995 | 1.0952 | 1.2105 | 1.614 | 1.8446
N2XH-O 1x95 RM | 15.8 | 34.049 | 0.88608 | 1.1392 | 1.3924 | 1.6456 | 1.8987 | 2.1519 | 2.4051 | 2.6582 | 3.5443 | 4.0506 | [6 empty] | N2XH-O 1x95 RM | 15.8 | 34.049 | 0.41117 | 0.52865 | 0.64613 | 0.76361 | 0.88108 | 0.99856 | 1.116 | 1.2335 | 1.6447 | 1.8796
N2XH-J 3x2,5 RE | 10.3 | 22.1965 | 1.3592 | 1.7476 | 2.1359 | 2.5243 | 2.9126 | 3.301 | 3.6893 | 4.0777 | 5.4369 | 6.2136 | [6 empty] | N2XH-J 3x2,5 RE | 10.3 | 22.1965 | 0.63073 | 0.81094 | 0.99115 | 1.1714 | 1.3516 | 1.5318 | 1.712 | 1.8922 | 2.5229 | 2.8833
N2XH-J 3x4 RE | 11.4 | 24.567 | 1.2281 | 1.5789 | 1.9298 | 2.2807 | 2.6316 | 2.9825 | 3.3333 | 3.6842 | 4.9123 | 5.614 | [6 empty] | N2XH-J 3x4 RE | 11.4 | 24.567 | 0.56987 | 0.73269 | 0.89551 | 1.0583 | 1.2212 | 1.384 | 1.5468 | 1.7096 | 2.2795 | 2.6051
N2XH-J 4x2,5 RE | 11.1 | 23.9205 | 1.2613 | 1.6216 | 1.982 | 2.3423 | 2.7027 | 3.0631 | 3.4234 | 3.7838 | 5.045 | 5.7658 | [6 empty] | N2XH-J 4x2,5 RE | 11.1 | 23.9205 | 0.58527 | 0.75249 | 0.91971 | 1.0869 | 1.2542 | 1.4214 | 1.5886 | 1.7558 | 2.3411 | 2.6755
N2XH-J 5x4 RE | 17 | 36.635 | 0.82353 | 1.0588 | 1.2941 | 1.5294 | 1.7647 | 2 | 2.2353 | 2.4706 | 3.2941 | 3.7647 | [6 empty] | N2XH-J 5x4 RE | 17 | 36.635 | 0.38215 | 0.49133 | 0.60052 | 0.7097 | 0.81889 | 0.92807 | 1.0373 | 1.1464 | 1.5286 | 1.747
N2XH-J 4x6 RE | 16 | 34.48 | 0.875 | 1.125 | 1.375 | 1.625 | 1.875 | 2.125 | 2.375 | 2.625 | 3.5 | 4 | [6 empty] | N2XH-J 4x6 RE | 16 | 34.48 | 0.40603 | 0.52204 | 0.63805 | 0.75406 | 0.87007 | 0.98608 | 1.1021 | 1.2181 | 1.6241 | 1.8561
N2XH-J 4x70 SM | 32.9 | 70.8995 | 0.42553 | 0.54711 | 0.66869 | 0.79027 | 0.91185 | 1.0334 | 1.155 | 1.2766 | 1.7021 | 1.9453 | [6 empty] | N2XH-J 4x70 SM | 32.9 | 70.8995 | 0.19746 | 0.25388 | 0.3103 | 0.36672 | 0.42313 | 0.47955 | 0.53597 | 0.59239 | 0.78985 | 0.90269
N2XH-O 1x16 | 8.3 | 17.8865 | 1.6867 | 2.1687 | 2.6506 | 3.1325 | 3.6145 | 4.0964 | 4.5783 | 5.0602 | 6.747 | 7.7108 | [6 empty] | N2XH-O 1x16 | 8.3 | 17.8865 | 0.78271 | 1.0063 | 1.23 | 1.4536 | 1.6772 | 1.9009 | 2.1245 | 2.3481 | 3.1309 | 3.5781
HSLCH-OZ 2x2,5 | 8.5 | 18.3175 | 1.6471 | 2.1176 | 2.5882 | 3.0588 | 3.5294 | 4 | 4.4706 | 4.9412 | 6.5882 | 7.5294 | [6 empty] | HSLCH-OZ 2x2,5 | 8.5 | 18.3175 | 0.7643 | 0.98267 | 1.201 | 1.4194 | 1.6378 | 1.8561 | 2.0745 | 2.2929 | 3.0572 | 3.4939
HSLH-JZ 12x1,5 | 13.2 | 28.446 | 1.0606 | 1.3636 | 1.6667 | 1.9697 | 2.2727 | 2.5758 | 2.8788 | 3.1818 | 4.2424 | 4.8485 | [6 empty] | HSLH-JZ 12x1,5 | 13.2 | 28.446 | 0.49216 | 0.63278 | 0.7734 | 0.91401 | 1.0546 | 1.1952 | 1.3359 | 1.4765 | 1.9686 | 2.2499
HSLH-JZ 5x1,5 | 8.9 | 19.1795 | 1.573 | 2.0225 | 2.4719 | 2.9213 | 3.3708 | 3.8202 | 4.2697 | 4.7191 | 6.2921 | 7.191 | [6 empty] | HSLH-JZ 5x1,5 | 8.9 | 19.1795 | 0.72995 | 0.9385 | 1.1471 | 1.3556 | 1.5642 | 1.7727 | 1.9813 | 2.1898 | 2.9198 | 3.3369
HSLCH-JZ 12x0,75 | 11.3 | 24.3515 | 1.2389 | 1.5929 | 1.9469 | 2.3009 | 2.6549 | 3.0088 | 3.3628 | 3.7168 | 4.9558 | 5.6637 | [6 empty] | HSLCH-JZ 12x0,75 | 11.3 | 24.3515 | 0.57491 | 0.73917 | 0.90344 | 1.0677 | 1.232 | 1.3962 | 1.5605 | 1.7247 | 2.2997 | 2.6282
HSLCH-JZ 4x0,75 | 7.75 | 16.7012 | 1.8065 | 2.3226 | 2.8387 | 3.3548 | 3.871 | 4.3871 | 4.9032 | 5.4194 | 7.2258 | 8.2581 | [6 empty] | HSLCH-JZ 4x0,75 | 7.75 | 16.7012 | 0.83826 | 1.0778 | 1.3173 | 1.5568 | 1.7963 | 2.0358 | 2.2753 | 2.5148 | 3.353 | 3.832
NA2XH-O 1x300 | 31.9 | 68.7445 | 0.43887 | 0.56426 | 0.68966 | 0.81505 | 0.94044 | 1.0658 | 1.1912 | 1.3166 | 1.7555 | 2.0063 | [6 empty] | NA2XH-O 1x300 | 31.9 | 68.7445 | 0.20365 | 0.26184 | 0.32003 | 0.37821 | 0.4364 | 0.49459 | 0.55277 | 0.61096 | 0.81461 | 0.93098
NA2XH-O 1x150 | 22.7 | 48.9185 | 0.61674 | 0.79295 | 0.96916 | 1.1454 | 1.3216 | 1.4978 | 1.674 | 1.8502 | 2.467 | 2.8194 | [6 empty] | NA2XH-O 1x150 | 22.7 | 48.9185 | 0.28619 | 0.36796 | 0.44973 | 0.5315 | 0.61326 | 0.69503 | 0.7768 | 0.85857 | 1.1448 | 1.3083
NA2XS(F)2Y 1x95/16 12/20 kV | 32 | 68.96 | 0.4375 | 0.5625 | 0.6875 | 0.8125 | 0.9375 | 1.0625 | 1.1875 | 1.3125 | 1.75 | 2 | [6 empty] | NA2XS(F)2Y 1x95/16 12/20 kV | 32 | 68.96 | 0.20302 | 0.26102 | 0.31903 | 0.37703 | 0.43503 | 0.49304 | 0.55104 | 0.60905 | 0.81206 | 0.92807
|  |  | 1- 7077000 | 2- 7078000 | 3- 7097000 | 4- 7097220 | 5- 7097260 | 6- 7097300 | 7- 7097340 | 8- 7098000 | 9- 7098100 | 10- 7099000 | [9 empty] | 1- 7077000 | 2- 7078000 | 3- 7097000 | 4- 7097220 | 5- 7097260 | 6- 7097300 | 7- 7097340 | 8- 7098000 | 9- 7098100 | 10- 7099000
|  | N2XH-O 1x95 RM | 0 | 1 | 1 | 1 | 1 | 0 | 3 | 4 | 4 | 4 | 2- 7078000 | [7 empty] | N2XH-O 1x95 RM | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 7- 7097340
|  | N2XH-J 3x2,5 RE | 1 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | N2XH-J 3x2,5 RE | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4- 7097220
|  | N2XH-J 3x4 RE | 1 | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | N2XH-J 3x4 RE | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 4- 7097220
|  | N2XH-J 4x2,5 RE | 1 | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | N2XH-J 4x2,5 RE | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 4- 7097220
|  | N2XH-J 5x4 RE | 0 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 2- 7078000 | [7 empty] | N2XH-J 5x4 RE | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 7- 7097340
|  | N2XH-J 4x6 RE | 0 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 2- 7078000 | [7 empty] | N2XH-J 4x6 RE | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 7- 7097340
|  | N2XH-J 4x70 SM | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 6- 7097300 | [7 empty] | N2XH-J 4x70 SM | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | nema
|  | N2XH-O 1x16 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | N2XH-O 1x16 | 0 | 1 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 2- 7078000
|  | HSLCH-OZ 2x2,5 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | HSLCH-OZ 2x2,5 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 3- 7097000
|  | HSLH-JZ 12x1,5 | 1 | 1 | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | HSLH-JZ 12x1,5 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 5- 7097260
|  | HSLH-JZ 5x1,5 | 1 | 2 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | HSLH-JZ 5x1,5 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 4 | 3- 7097000
|  | HSLCH-JZ 12x0,75 | 1 | 1 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | HSLCH-JZ 12x0,75 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 3 | 4 | 4- 7097220
|  | HSLCH-JZ 4x0,75 | 1 | 3 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 1- 7077000 | [7 empty] | HSLCH-JZ 4x0,75 | 0 | 1 | 1 | 1 | 1 | 2 | 3 | 4 | 4 | 4 | 2- 7078000
|  | NA2XH-O 1x300 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 6- 7097300 | [7 empty] | NA2XH-O 1x300 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | nema
|  | NA2XH-O 1x150 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 1 | 4 | 4 | 4- 7097220 | [7 empty] | NA2XH-O 1x150 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 9- 7098100
|  | NA2XS(F)2Y 1x95/16 12/20 kV | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 2 | 6- 7097300 | [7 empty] | NA2XS(F)2Y 1x95/16 12/20 kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | nema